SPARC SuperCluster T4-4

Site Checklists

Part No. E21663-05

February 2012

Copyright © 2011, 2012, Oracle and/or its affiliates. All rights reserved.

This software and related documentation are provided under a license agreement containing restrictions on use and disclosure and are protected by intellectual property laws. Except as expressly permitted in your license agreement or allowed by law, you may not use, copy, reproduce, translate, broadcast, modify, license, transmit, distribute, exhibit, perform, publish, or display any part, in any form, or by any means. Reverse engineering, disassembly, or decompilation of this software, unless required by law for interoperability, is prohibited.

The information contained herein is subject to change without notice and is not warranted to be error-free. If you find any errors, please report them to us in writing.

If this is software or related software documentation that is delivered to the U.S. Government or anyone licensing it on behalf of the U.S. Government, the following notice is applicable:

U.S. GOVERNMENT RIGHTS Programs, software, databases, and related documentation and technical data delivered to U.S. Government customers are "commercial computer software" or "commercial technical data" pursuant to the applicable Federal Acquisition Regulation and agency-specific supplemental regulations. As such, the use, duplication, disclosure, modification, and adaptation shall be subject to the restrictions and license terms set forth in the applicable Government contract, and, to the extent applicable by the terms of the Government contract, the additional rights set forth in FAR 52.227-19, Commercial Computer Software License (December 2007). Oracle America, Inc., 500 Oracle Parkway, Redwood City, CA 94065.

This software or hardware is developed for general use in a variety of information management applications. It is not developed or intended for use in any inherently dangerous applications, including applications which may create a risk of personal injury. If you use this software or hardware in dangerous applications, then you shall be responsible to take all appropriate fail-safe, backup, redundancy, and other measures to ensure its safe use. Oracle Corporation and its affiliates disclaim any liability for any damages caused by use of this software or hardware in dangerous applications.

Oracle and Java are registered trademarks of Oracle and/or its affiliates. Other names may be trademarks of their respective owners.

AMD, Opteron, the AMD logo, and the AMD Opteron logo are trademarks or registered trademarks of Advanced Micro Devices. Intel and Intel Xeon are trademarks or registered trademarks of Intel Corporation. All SPARC trademarks are used under license and are trademarks or registered trademarks of SPARC International, Inc. UNIX is a registered trademark of The Open Group.

This software or hardware and documentation may provide access to or information on content, products, and services from third parties. Oracle Corporation and its affiliates are not responsible for and expressly disclaim all warranties of any kind with respect to third-party content, products, and services. Oracle Corporation and its affiliates will not be responsible for any loss, costs, or damages incurred due to your access to or use of third-party content, products, or services.

Copyright © 2011, 2012, Oracle et/ou ses affiliés. Tous droits réservés.

Ce logiciel et la documentation qui l'accompagne sont protégés par les lois sur la propriété intellectuelle. Ils sont concédés sous licence et soumis à des restrictions d'utilisation et de divulgation. Sauf disposition de votre contrat de licence ou de la loi, vous ne pouvez pas copier, reproduire, traduire, diffuser, modifier, breveter, transmettre, distribuer, exposer, exécuter, publier ou afficher le logiciel, même partiellement, sous quelque forme et par quelque procédé que ce soit. Par ailleurs, il est interdit de procéder à toute ingénierie inverse du logiciel, de le désassembler ou de le décompiler, excepté à des fins d'interopérabilité avec des logiciels tiers ou tel que prescrit par la loi.

Les informations fournies dans ce document sont susceptibles de modification sans préavis. Par ailleurs, Oracle Corporation ne garantit pas qu'elles soient exemptes d'erreurs et vous invite, le cas échéant, à lui en faire part par écrit.

Si ce logiciel, ou la documentation qui l'accompagne, est concédé sous licence au Gouvernement des Etats-Unis, ou à toute entité qui délivre la licence de ce logiciel ou l'utilise pour le compte du Gouvernement des Etats-Unis, la notice suivante s'applique :

U.S. GOVERNMENT RIGHTS Programs, software, databases, and related documentation and technical data delivered to U.S. Government customers are "commercial computer software" or "commercial technical data" pursuant to the applicable Federal Acquisition Regulation and agency-specific supplemental regulations.  As such, the use, duplication, disclosure, modification, and adaptation shall be subject to the restrictions and license terms set forth in the applicable Government contract, and, to the extent applicable by the terms of the Government contract, the additional rights set forth in FAR 52.227-19, Commercial Computer Software License (December 2007).  Oracle America, Inc., 500 Oracle Parkway, Redwood City, CA 94065.

Ce logiciel ou matériel a été développé pour un usage général dans le cadre d'applications de gestion des informations. Ce logiciel ou matériel n'est pas conçu ni n'est destiné à être utilisé dans des applications à risque, notamment dans des applications pouvant causer des dommages corporels. Si vous utilisez ce logiciel ou matériel dans le cadre d'applications dangereuses, il est de votre responsabilité de prendre toutes les mesures de secours, de sauvegarde, de redondance et autres mesures nécessaires à son utilisation dans des conditions optimales de sécurité. Oracle Corporation et ses affiliés déclinent toute responsabilité quant aux dommages causés par l'utilisation de ce logiciel ou matériel pour ce type d'applications.

Oracle et Java sont des marques déposées d'Oracle Corporation et/ou de ses affiliés. Tout autre nom mentionné peut correspondre à des marques appartenant à d'autres propriétaires qu'Oracle.

AMD, Opteron, le logo AMD et le logo AMD Opteron sont des marques ou des marques déposées d'Advanced Micro Devices. Intel et Intel Xeon sont des marques ou des marques déposées d'Intel Corporation. Toutes les marques SPARC sont utilisées sous licence et sont des marques ou des marques déposées de SPARC International, Inc. UNIX est une marque déposée d'The Open Group.

Ce logiciel ou matériel et la documentation qui l'accompagne peuvent fournir des informations ou des liens donnant accès à des contenus, des produits et des services émanant de tiers. Oracle Corporation et ses affiliés déclinent toute responsabilité ou garantie expresse quant aux contenus, produits ou services émanant de tiers. En aucun cas, Oracle Corporation et ses affiliés ne sauraient être tenus pour responsables des pertes subies, des coûts occasionnés ou des dommages causés par l'accès à des contenus, produits ou services tiers, ou à leur utilisation.

Content

Using This Documentation	4

Related Documentation	4

Feedback	4

Support and Accessibility	4

SPARC SuperCluster T4-4 Site Checklists	5

System Components Checklist	5

Data Center Room Checklist	6

Data Center Environment Checklist	8

Access Route Checklist	9

Facility Power Checklist	11

Safety Checklist	13

Logistics Checklist	14

Network Configuration Checklist	16

Database High Availability Checklist	17

Exadata Storage Server Storage Capacity Checklist	18

Auto Service Request Checklist	20

Preface

Using This Documentation

This guide provides the site checklists that must be completed before receiving the SPARC SuperCluster T4-4.

# Related Documentation

| Description | Links |
| --- | --- |
| All Oracle products | http://oracle.com/documentation |

# Feedback

Provide feedback on this documentation at:

http://www.oracle.com/goto/docfeedback

# Support and Accessibility

| Description | Links |
| --- | --- |
| Access electronic support through My Oracle Support | http://support.oracle.com |
|  | For hearing impaired: http://www.oracle.com/accessibility/support.html |
| Learn about Oracle’s commitment to accessibility | http://www.oracle.com/us/corporate/accessibility/index.html |

Chapter

1

SPARC SuperCluster T4-4 Site Checklists

Complete the checklists in this chapter to ensure that the site is prepared for installing and deploying SPARC SuperCluster T4-4.

- Data Center Room Checklist

- Data Center Environment Checklist

- Access Route Checklist

- Facility Power Checklist

- Safety Checklist

- Logistics Checklist

- Network Configuration Checklist

- Database High Availability Checklist

- Exadata Storage Server Storage Capacity Checklist

- Auto Service Request Checklist

# System Components Checklist

Complete the following checklist to ensure that the systems component considerations have been addressed.

| System Components Checklist Items | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Is it a SPARC SuperCluster T4-4 or Oracle Exadata Storage Expansion Rack? |  |  |  |  |
| How many racks will be installed? |  |  |  |  |
| If more than one rack will be installed, then was the cable upgrade kit ordered? |  |  |  |  |
| Is the rack installation a new system or an addition to an existing system? |  |  |  |  |
| Are all SPARC SuperCluster T4-4 racks adjacent to each other? |  |  |  |  |
| If the connecting racks are not within the specified proximity, then have the following been done: - Purchased approved longer InfiniBand cables from an approved third-party provider? - Asked Oracle Support Services to provide and schedule the custom multi-rack cabling service with the installation? |  |  |  |  |
| Will the Ethernet switch be replaced? If yes, then have you arranged for the replacement switch installation? |  |  |  |  |

# Data Center Room Checklist

Complete the following checklist to ensure that the data center room requirements are met. For information about the data center requirements, see “Site Requirements for SPARC  SuperCluster T4-4” in the SPARC SuperCluster T4-4 Owner’s Guide.

| Data Center Room Checklist Items | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Has the SPARC SuperCluster T4-4 location been allocated? |  |  |  |  |
| Is there a vacant location for the new equipment? |  |  |  |  |
| Does the floor layout meet the equipment maintenance access requirements? |  |  |  |  |
| Is there adequate space available for maintenance? |  |  |  |  |
| Will the equipment be positioned so that the exhaust air of one rack does not enter the air inlet of another rack? |  |  |  |  |
| Have cabinet stabilization measures been considered? |  |  |  |  |
| Does the raised floor satisfy the weight requirements for the new hardware? - Shipping weight: - Full rack: 1009.2 kg (2225 lbs) - Half rack: 721 kg (1586 lbs) - Standard weight: - Full rack: 862 kg (1900 lbs) - Half rack: 594 kg (1310 lbs) |  |  |  |  |
| Can floor tiles be removed without permission to accommodate service? |  |  |  |  |
| Are there cable routing channels or cutouts? |  |  |  |  |
| Are you providing any additional hardware? |  |  |  |  |
| Is the hardware you are providing fully compatible with the SPARC SuperCluster T4-4? |  |  |  |  |
| Will the new hardware location require any non-standard cable lengths? |  |  |  |  |
| Is the floor to ceiling height a minimum of 2914 mm or 2.9 m (9.6 feet)? |  |  |  |  |
| Is the depth of the raised floor a minimum of 46 cm (18 inches)? |  |  |  |  |

# Data Center Environment Checklist

Complete the following checklist to ensure that the data center environment requirements are met. For information about environment requirements, see “Site Requirements for SPARC  SuperCluster T4-4” in the SPARC SuperCluster T4-4 Owner’s Guide.

| Data Center Environment Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Does the computer room air handling meet temperature and humidity requirements? |  |  |  |  |
| Does the installation floor layout satisfy the ventilation requirements? |  |  |  |  |
| Will the equipment be positioned so the exhaust air of one rack does not enter the air intake of another rack? |  |  |  |  |
| Are the perforated floor tiles each rated at 400 CFM or greater? |  |  |  |  |
| Do the data center air conditioners provide sufficient front to back airflow? - SPARC SuperCluster T4-4 Full Rack: 2,498 CFM (maximum) - SPARC SuperCluster T4-4 Half Rack: 1,417 CFM (maximum) - Oracle Exadata Storage Expansion Rack Full Rack: 1,980 CFM (maximum) - Oracle Exadata Storage Expansion Rack Half Rack: 1,090 CFM (maximum) - Oracle Exadata Storage Expansion Rack Quarter Rack: 530 CFM (maximum) |  |  |  |  |
| Is airflow adequate to prevent hot spots? |  |  |  |  |
| Can the data center continuously satisfy environmental requirements? - SPARC SuperCluster T4-4 Full Rack: 53,966 BTU/hour (maximum) - SPARC SuperCluster T4-4 Half Rack: 30,610 BTU/hour (maximum) - Oracle Exadata Storage Expansion Rack Full Rack: 43,000 BTU/hour (maximum) - Oracle Exadata Storage Expansion Rack Half Rack: 23,600 BTU/hour (maximum) - Oracle Exadata Storage Expansion Rack Quarter Rack: 11,600 BTU/hour (maximum) |  |  |  |  |
| Can more vented floor tiles be obtained if required? |  |  |  |  |

# Access Route Checklist

Complete the following checklist to ensure that the access route requirements are met.

| Access Route Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Has the access route been checked for clearances of the packaged equipment? |  |  |  |  |
| Do all the doors and entry ways conform to the width and height requirements for transportation, including the width of the unpacked unit? |  |  |  |  |
| Do all the doors meet the height requirement of minimum 86 inches for packaged delivery? |  |  |  |  |
| Does the access route provide sufficient space for transport of the packed devices? |  |  |  |  |
| Are there any ramps or thresholds that are of concern? If yes, provide details. |  |  |  |  |
| Are there any stairs or ramps in the moving patch for the new hardware? |  |  |  |  |
| Have you confirmed that all route incline angles are within the permitted range? |  |  |  |  |
| Have you confirmed that the access route is free of any obstacles that would expose the device to shock? |  |  |  |  |
| Are all the surfaces acceptable for rolling the new unpacked and packed equipment? |  |  |  |  |
| If a pallet jack is to be used, have you confirmed the following: - The pallet jack supports the device weight? - The pallet jack tines are compatible with the shipping pallet? Following are the weights for the SPARC SuperCluster T4-4: - Shipping weight: - Full rack: 1009.2 kg (2225 lbs) - Half rack: 721 kg (1586 lbs) - Standard weight: - Full rack: 862 kg (1900 lbs) - Half rack: 594 kg (1310 lbs) Following are the weights for the Oracle Exadata Storage Expansion Rack: - Shipping weight: - Full rack: 1001.1 kg (2207 lbs) - Half rack: 659 kg (1454 lbs) - Quarter rack: 475.3 kg (1048 lbs) - Standard weight: - Full rack: 917.6 kg (2023 lbs) - Half rack: 578.3 kg (1275 lbs) - Quarter rack: 396.8 kg (875 lbs) |  |  |  |  |
| If there are stairs, then is a loading elevator accessible for the equipment? |  |  |  |  |
| If an elevator is to be used, have you confirmed the following: - The elevator car is wide enough for the device to be carried into it? - The elevator car is high enough for the device to be carried into it? - The load limit of the elevator is greater than the device weight? - Are elevators available to handle up to 862 kg (1900 lbs) for the full rack or 594 kg (1310 lbs) for the half rack? - The elevator door meets the minimum height requirement of 86 inches for packaged rack delivery? |  |  |  |  |
| Does the path from the receiving location to the designated data center area support the weight of the unpacked equipment? |  |  |  |  |
| Is the path onto the raised floor rated for dynamic loading of the server? Refer to “Site Requirements for SPARC SuperCluster T4-4” in the SPARC SuperCluster T4-4 Owner’s Guide for requirements. |  |  |  |  |

# Facility Power Checklist

Complete the following checklist to ensure that the facility power requirements are met. For information about power requirements, see “Site Requirements for SPARC SuperCluster T4-4” in the SPARC SuperCluster T4-4 Owner’s Guide.

| Facility Power Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Do you know the required operating voltage and electric current level of the device and peripherals? |  |  |  |  |
| Will you be using single-phase (low-voltage or high-voltage) or 3-phase (low-voltage or high-voltage) power? |  |  |  |  |
| Are enough power outlets provided within 2 meters for each rack? |  |  |  |  |
| Do the power outlets have appropriate socket receptacles for the PDU option ordered? Options are: - Low-voltage 22 kVA single-phase - High-voltage 22 kVA single-phase - Low-voltage 24 kVA three-phase - High-voltage 24 kVA three-phase |  |  |  |  |
| Will optional ground cables be attached to the rack? |  |  |  |  |
| Are the circuit breakers for the equipment suitable in terms of voltage and current-carrying capacities? |  |  |  |  |
| Does the power frequency meet the equipment specifications? |  |  |  |  |
| Are power outlets available for the new equipment at the designated location? |  |  |  |  |
| Will system power be delivered from two separate grids? |  |  |  |  |
| Is there a UPS to power the equipment? |  |  |  |  |
| Is the capacity of the UPS sufficient for the SPARC SuperCluster T4-4? |  |  |  |  |
| Do you have the minimum required power sources to support the power load for the new hardware? Use kilowatt (kW) /kilovolt (kVA) to express power load. - SPARC SuperCluster T4-4 Full Rack: Maximum: 15.02 kW (15.81 kVA) - SPARC SuperCluster T4-4 Half Rack: Maximum: 8.52 kW (8.97 kVA) - Oracle Exadata Storage Expansion Rack Full Rack: Maximum: 12.6 kW (12.9 kVA) - Oracle Exadata Storage Expansion Rack Half Rack: Maximum: 6.9 kW (7.1 kVA) - Oracle Exadata Storage Expansion Rack Quarter Rack: Maximum: 3.4 kW (3.5 kVA) |  |  |  |  |

# Safety Checklist

Complete the following checklist to ensure that the safety requirements are met. For information about safety, see “Site Requirements for SPARC SuperCluster T4-4” in the SPARC SuperCluster T4-4 Owner’s Guide.

| Safety Checklist Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Is there an emergency power shut off? |  |  |  |  |
| Is there a fire protection system in the data center room? |  |  |  |  |
| Is the computer room adequately equipped to extinguish a fire? |  |  |  |  |
| Is antistatic flooring installed? |  |  |  |  |
| Is the floor below the raised floor free of obstacles and blockages? |  |  |  |  |

# Logistics Checklist

Complete the following checklist to ensure that the logistics requirements are met. For information about unpacking and space requirements, see “Site Requirements for SPARC SuperCluster T4-4” in the SPARC SuperCluster T4-4 Owner’s Guide.

| Logistics Checklist Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Do you have contact information for the data center personnel? |  |  |  |  |
| Is there security or access control for the data center? |  |  |  |  |
| Are there any security background checks or security clearances required for vendor personnel to access the data center? If yes, do you have a recommended agency? |  |  |  |  |
| How many days in advance must background checks be completed? |  |  |  |  |
| Are there any additional security access issues? |  |  |  |  |
| Is computer room access available for installation personnel? |  |  |  |  |
| Are laptops, cell phones, and cameras allowed in the data center? |  |  |  |  |
| Does the building have a delivery dock? |  |  |  |  |
| Is there a delivery/unpacking/staging area? |  |  |  |  |
| Is the delivery inside? |  |  |  |  |
| If the delivery is not inside, then is the site prepared for uncrating? |  |  |  |  |
| Is the unpacking/staging area protected from the elements? |  |  |  |  |
| Does the building have adequate receiving space? |  |  |  |  |
| Is the unpacking area air-conditioned to avoid thermal shock for various hardware components? |  |  |  |  |
| Will sufficient moving personnel be available to install the hardware? |  |  |  |  |
| Is union labor required for any part of the delivery or installation? |  |  |  |  |
| Are you prepared for uncrating and trash removal? |  |  |  |  |
| Is uncrating of cabinet and cabinet trash removal required? |  |  |  |  |
| Are there any restrictions on delivery truck length, width, or height? |  |  |  |  |
| Does the customer allow cardboard boxes and other packing material in the computer room? If no, then do ground-level deliveries require a truck with a side rail lift? |  |  |  |  |
| Is there a time constraint on dock access? If yes, provide time constraints. |  |  |  |  |
| Is tail lift required on delivery carrier to unload the equipment at the delivery dock? |  |  |  |  |
| Will any of the following be required to place equipment in computer room? - Stair walkers - Lifters - Ramps - Steel plates - Floor covers |  |  |  |  |
| Does the delivery carrier require any special equipment, such as non-floor damaging rollers, transport dollies, pallet jacks or fork lifts? |  |  |  |  |

# Network Configuration Checklist

Complete the following checklist to ensure that the network configuration requirements are met for the following networks in the SPARC SuperCluster T4-4:

- InfiniBand network: Used for communication between components installed in the SPARC SuperCluster T4-4

- Client access network: 10 GbE network, with connections to the 10 GbE network interface cards in the SPARC T4-4 servers

- ILOM management network: ILOM network, with connections to the ILOM (NET MGT) port on the SPARC T4-4 servers, Exadata Storage Servers and Sun ZFS Storage 7320 appliance

- Host management network: 1 GbE network, with connections to the NET0-3 port on the SPARC T4-4 servers, and the NET0 port to the Exadata Storage Servers and Sun ZFS Storage 7320 appliance

For information about IP addresses, see “Understanding the Network Requirements for the  SPARC SuperCluster T4-4” in the SPARC SuperCluster T4-4 Owner’s Guide.

| Network Specification Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Were any conflicts found while running the checkip.sh script before connecting the network? See “Understanding the Network Requirements for the SPARC SuperCluster T4-4” in the SPARC SuperCluster T4-4 Owner’s Guide for information on the script. |  |  |  |  |
| Were any conflicts found while running the checkip.sh script after initial configuration? See “Understanding the Network Requirements for the SPARC SuperCluster T4-4” in the SPARC SuperCluster T4-4 Owner’s Guide for information on the script. |  |  |  |  |
| Do you have the appropriate number of network drops available for the SPARC SuperCluster T4-4? 10 GbE client access network: - Full rack: - Typical: 8 network drops - Maximum: 32 network drops - Half rack: - Typical: 4 network drops - Maximum: 16 network drops 1 GbE management network: - Full rack: 1 network drop - Half rack: 1 network drop |  |  |  |  |
| Did you run the required network cables from your network equipment to the location where SPARC SuperCluster T4-4 will be installed? |  |  |  |  |
| Did you label the network cables that will connect to SPARC SuperCluster T4-4? |  |  |  |  |
| Have the optional 10 GbE QSFP transceivers and appropriate fiber cables been ordered? |  |  |  |  |
| Will the Cisco Ethernet switch have IP routing disabled? |  |  |  |  |
| Do you have the appropriate number of IP addresses reserved for the SPARC SuperCluster T4-4? See the SPARC SuperCluster T4-4 Half Rack Configuration Worksheets or the SPARC SuperCluster T4-4 Full Rack Configuration Worksheets for more information. |  |  |  |  |

# Database High Availability Checklist

Complete the following checklist to ensure the requirements for high availability are met for SPARC SuperCluster T4-4. For additional information about high availability, see Oracle Database High Availability Overview.

| Database High Availability Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Have high redundancy disk groups been configured for best protection against different storage failures and corruptions? |  |  |  |  |
| Will the pre-optimized and configured database be used after deployment? |  |  |  |  |
| Have you reviewed the Oracle Exadata Storage Server Software patching overview and patch testing guidelines in My Oracle Support note 1262380.1? |  |  |  | - |
| Have you reviewed the Oracle Exadata Storage Server Software Maximum Availability Architecture (MAA) web site for post-deployment steps to achieve MAA? The Web site is available at http://www.oracle.com/goto/maa |  |  |  |  |

# Exadata Storage Server Storage Capacity Checklist

Complete the checklist in this section to determine if the amount of storage in the Exadata Storage Servers in the SPARC SuperCluster T4-4 or Oracle Exadata Storage Expansion Rack is sufficient for your needs. The following tables provide the amount of storage available in each type of rack, depending on ASM normal or high redundancy. The values in the following tables are based on these disk capacities:

- High performance disks: 600 MB

- High capacity disks: 3 TB

| Exadata Storage Server Storage Capacity: SPARC SuperCluster T4-4 | Half Rack | Full Rack |
| --- | --- | --- |
| Raw disk capacity | - High performance disk: 21.6 TB - High capacity disk: 108 TB | - High performance disk: 43.2 TB - High capacity disk: 216 TB |
| Raw flash capacity | 1.1 TB | 2.2 TB |
| Usable mirrored capacity (ASM normal redundancy) | - High performance disk: 9.5 TB - High capacity disk: 47 TB | - High performance disk: 19 TB - High capacity disk: 94.5 TB |
| Usable triple mirrored capacity (ASM high redundancy) | N/A | - High performance disk: 13 TB - High capacity disk: 64.5 TB |

| Exadata Storage Server Storage Capacity: Oracle Exadata Storage Expansion Rack, High Capacity Version | Quarter Rack | Half Rack | Full Rack |
| --- | --- | --- | --- |
| Raw disk capacity | 144 TB | 324 TB | 648 TB |
| Raw flash capacity | 1.5 TB | 3.4 TB | 6.75 TB |
| Usable mirrored capacity (ASM normal redundancy) | 64 TB | 144 TB | 288 TB |
| Usable triple mirrored capacity (ASM high redundancy) | 43 TB | 97 TB | 193.5 TB |

| Exadata Storage Server Storage Capacity: Oracle Exadata Storage Expansion Rack, High Performance Version | Quarter Rack | Half Rack | Full Rack |
| --- | --- | --- | --- |
| Raw disk capacity | 28 TB | 64 TB | 128 TB |
| Raw flash capacity | 1.5 TB | 3.4 TB | 6.75 TB |
| Usable mirrored capacity (ASM normal redundancy) | 13 TB | 29 TB | 58 TB |
| Usable triple mirrored capacity (ASM high redundancy) | 8 TB | 19 TB | 39 TB |

| Exadata Storage Server Storage Capacity Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Does the SPARC SuperCluster T4-4 have the storage capacity that you need for the Exadata Storage Servers? |  |  |  |  |
| Does the Oracle Exadata Storage Expansion Rack have the storage capacity that you need for the Exadata Storage Servers? |  |  |  |  |

# Auto Service Request Checklist

Complete the following checklist if you are planning to use Auto Service Request with SPARC SuperCluster T4-4. For additional information about Auto Service Request, see “Maintaining the SPARC SuperCluster T4-4” in the SPARC SuperCluster T4-4 Owner’s Guide.

| ASR Service Request Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Do you have a My Oracle Support to register Auto Service Request? |  |  |  |  |
| Do you have your Oracle Support Customer Support Identifier (CSI) number? |  |  |  |  |
| Will you be using a standalone server for the ASR Manager? If yes, then you must have the standalone server available before the Oracle installers arrive on site. |  |  |  |  |
| Do you have the host name and IP address for the server that will have ASR Manager? |  |  |  |  |
| Will the system need a proxy server? If so, what is the host name and IP address for the proxy server? |  |  |  |  |
| Do you have the technical contact information for Auto Service Request? This information should include the first name, last name, and email address of the contact. |  |  |  |  |
| Do you have Oracle Auto Service Request Release 3.5 or later? If not, go to http://www.oracle.com/asr and click on the Downloads link to download the latest version of Oracle Auto Service Request. |  |  |  |  |