Oracle® SuperCluster M8 and SuperCluster M7 Site Checklists

Part No. E58631-04

January 2019

Copyright © 2015, 2019, Oracle and/or its affiliates. All rights reserved.

This software and related documentation are provided under a license agreement containing restrictions on use and disclosure and are protected by intellectual property laws. Except as expressly permitted in your license agreement or allowed by law, you may not use, copy, reproduce, translate, broadcast, modify, license, transmit, distribute, exhibit, perform, publish, or display any part, in any form, or by any means. Reverse engineering, disassembly, or decompilation of this software, unless required by law for interoperability, is prohibited.

The information contained herein is subject to change without notice and is not warranted to be error-free. If you find any errors, please report them to us in writing.

If this is software or related documentation that is delivered to the U.S. Government or anyone licensing it on behalf of the U.S. Government, then the following notice is applicable:

U.S. GOVERNMENT END USERS. Oracle programs, including any operating system, integrated software, any programs installed on the hardware, and/or documentation, delivered to U.S. Government end users are "commercial computer software" pursuant to the applicable Federal Acquisition Regulation and agency-specific supplemental regulations. As such, use, duplication, disclosure, modification, and adaptation of the programs, including any operating system, integrated software, any programs installed on the hardware, and/or documentation, shall be subject to license terms and license restrictions applicable to the programs. No other rights are granted to the U.S. Government.

This software or hardware is developed for general use in a variety of information management applications. It is not developed or intended for use in any inherently dangerous applications, including applications that may create a risk of personal injury. If you use this software or hardware in dangerous applications, then you shall be responsible to take all appropriate fail-safe, backup, redundancy, and other measures to ensure its safe use. Oracle Corporation and its affiliates disclaim any liability for any damages caused by use of this software or hardware in dangerous applications.

Oracle and Java are registered trademarks of Oracle and/or its affiliates. Other names may be trademarks of their respective owners.

Intel and Intel Xeon are trademarks or registered trademarks of Intel Corporation. All SPARC trademarks are used under license and are trademarks or registered trademarks of SPARC International, Inc. AMD, Opteron, the AMD logo, and the AMD Opteron logo are trademarks or registered trademarks of Advanced Micro Devices. UNIX is a registered trademark of The Open Group.

This software or hardware and documentation may provide access to or information about content, products, and services from third parties. Oracle Corporation and its affiliates are not responsible for and expressly disclaim all warranties of any kind with respect to third-party content, products, and services unless otherwise set forth in an applicable agreement between you and Oracle. Oracle Corporation and its affiliates will not be responsible for any loss, costs, or damages incurred due to your access to or use of third-party content, products, or services, except as set forth in an applicable agreement between you and Oracle.

Documentation Accessibility

For information about Oracle's commitment to accessibility, visit the Oracle Accessibility Program website at http://www.oracle.com/pls/topic/lookup?ctx=acc&#x0026;id=docacc.

Access to Oracle Support

Oracle customers that have purchased support have access to electronic support through My Oracle Support. For information, visit http://www.oracle.com/pls/topic/lookup?ctx=acc&#x0026;id=info or visit http://www.oracle.com/pls/topic/lookup?ctx=acc&#x0026;id=trs if you are hearing impaired.

Copyright © 2015, 2019, Oracle et/ou ses affiliés. Tous droits réservés.

Ce logiciel et la documentation qui l’accompagne sont protégés par les lois sur la propriété intellectuelle. Ils sont concédés sous licence et soumis à des restrictions d’utilisation et de divulgation. Sauf stipulation expresse de votre contrat de licence ou de la loi, vous ne pouvez pas copier, reproduire, traduire, diffuser, modifier, breveter, transmettre, distribuer, exposer, exécuter, publier ou afficher le logiciel, même partiellement, sous quelque forme et par quelque procédé que ce soit. Par ailleurs, il est interdit de procéder à toute ingénierie inverse du logiciel, de le désassembler ou de le décompiler, excepté à des fins d’interopérabilité avec des logiciels tiers ou tel que prescrit par la loi.

Les informations fournies dans ce document sont susceptibles de modification sans préavis. Par ailleurs, Oracle Corporation ne garantit pas qu’elles soient exemptes d’erreurs et vous invite, le cas échéant, à lui en faire part par écrit.

Si ce logiciel, ou la documentation qui l’accompagne, est concédé sous licence au Gouvernement des Etats-Unis, ou à toute entité qui délivre la licence de ce logiciel ou l’utilise pour le compte du Gouvernement des Etats-Unis, la notice suivante s’applique:

U.S. GOVERNMENT END USERS. Oracle programs, including any operating system, integrated software, any programs installed on the hardware, and/or documentation, delivered to U.S. Government end users are "commercial computer software" pursuant to the applicable Federal Acquisition Regulation and agency-specific supplemental regulations. As such, use, duplication, disclosure, modification, and adaptation of the programs, including any operating system, integrated software, any programs installed on the hardware, and/or documentation, shall be subject to license terms and license restrictions applicable to the programs. No other rights are granted to the U.S. Government.

Ce logiciel ou matériel a été développé pour un usage général dans le cadre d’applications de gestion des informations. Ce logiciel ou matériel n’est pas conçu ni n’est destiné à être utilisé dans des applications à risque, notamment dans des applications pouvant causer des dommages corporels. Si vous utilisez ce logiciel ou matériel dans le cadre d’applications dangereuses, il est de votre responsabilité de prendre toutes les mesures de secours, de sauvegarde, de redondance et autres mesures nécessaires à son utilisation dans des conditions optimales de sécurité. Oracle Corporation et ses affiliés déclinent toute responsabilité quant aux dommages causés par l’utilisation de ce logiciel ou matériel pour ce type d’applications.

Oracle et Java sont des marques déposées d’Oracle Corporation et/ou de ses affiliés. Tout autre nom mentionné peut correspondre à des marques appartenant à d’autres propriétaires qu’Oracle.

Intel et Intel Xeon sont des marques ou des marques déposées d’Intel Corporation. Toutes les marques SPARC sont utilisées sous licence et sont des marques ou des marques déposées de SPARC International, Inc. AMD, Opteron, le logo AMD et le logo AMD Opteron sont des marques ou des marques déposées d’Advanced Micro Devices. UNIX est une marque déposée d’The Open Group.

Ce logiciel ou matériel et la documentation qui l’accompagne peuvent fournir des informations ou des liens donnant accès à des contenus, des produits et des services émanant de tiers. Oracle Corporation et ses affiliés déclinent toute responsabilité ou garantie expresse quant aux contenus, produits ou services émanant de tiers, sauf mention contraire stipulée dans un contrat entre vous et Oracle. En aucun cas, Oracle Corporation et ses affiliés ne sauraient être tenus pour responsables des pertes subies, des coûts occasionnés ou des dommages causés par l’accès à des contenus, produits ou services tiers, ou à leur utilisation, sauf mention contraire stipulée dans un contrat entre vous et Oracle.

Accessibilité de la documentation

Pour plus d’informations sur l’engagement d’Oracle pour l’accessibilité à la documentation, visitez le site Web Oracle Accessibility Program, à l’adresse http://www.oracle.com/pls/topic/lookup?ctx=acc&#x0026;id=docacc.

Accès au support électronique

Les clients Oracle qui ont souscrit un contrat de support ont accès au support électronique via My Oracle Support. Pour plus d’informations, visitez le site http://www.oracle.com/pls/topic/lookup?ctx=acc&#x0026;id=info ou le site http://www.oracle.com/pls/topic/lookup?ctx=acc&#x0026;id=trs si vous êtes malentendant.

Contents

Using This Documentation	7

Product Documentation Library	7

Feedback	7

SuperCluster M8 and SuperCluster M7 Site Checklists	9

System Components Checklist	9

Data Center Room Checklist	11

Data Center Environment Checklist	14

Access Route Checklist	18

Facility Power Checklist	20

Safety Checklist	22

Logistics Checklist	23

Network Configuration Checklist	25

Database High Availability Checklist	27

Storage Server Storage Capacity Checklist	28

Auto Service Request Checklist	30

Oracle Enterprise Manager Ops Center Checklist	31

Using This Documentation

Overview –  Provides the site checklists that must be completed before receiving SuperCluster M8 or SuperCluster M7

Audience – Technicians, system administrators, and authorized service providers

Required knowledge – Experience with SuperCluster systems

# Product Documentation Library

Documentation and resources for this product and related products are available at http://www.oracle.com/goto/sc-m7/docs.

# Feedback

Provide feedback about this documentation at http://www.oracle.com/goto/docfeedback.

Chapter

1

SuperCluster M8 and SuperCluster M7 Site Checklists

Complete the checklists in this chapter to ensure that the site is prepared for installing and deploying the SuperCluster system.

System Components Checklist

Data Center Room Checklist

Data Center Environment Checklist

Access Route Checklist

Facility Power Checklist

Safety Checklist

Logistics Checklist

Network Configuration Checklist

Database High Availability Checklist

Storage Server Storage Capacity Checklist

Auto Service Request Checklist

# System Components Checklist

Complete the following checklist to ensure that the systems component considerations have been addressed.

| System Components Checklist Items | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Is it a SuperCluster system or Oracle Exadata Storage Expansion Rack? |  |  |  |  |
| How many racks will be installed? |  |  |  |  |
| If more than one rack will be installed, was the cable upgrade kit ordered? InfiniBand cables to connect three racks are included in the rack spares kit. Additional optical InfiniBand cables are required when connecting four or more racks. |  |  |  |  |
| Is the rack installation a new system or an addition to an existing system? |  |  |  |  |
| Are all SuperCluster systems adjacent to each other? |  |  |  |  |
| If the connecting racks are not within the specified proximity, have the following been done: Purchased approved longer InfiniBand cables from an approved third-party provider? Asked Oracle Support Services to provide and schedule the custom multi-rack cabling service with the installation? |  |  |  |  |
| Will the Ethernet switch be replaced? If yes, have you arranged for the replacement switch installation? |  |  |  |  |

# Data Center Room Checklist

Complete the following checklist to ensure that the data center room requirements are met. For information about the data center requirements, see “Preparing the Site” in the installation guide that came with your system.

| Data Center Room Checklist Items | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Has a vacant system location been allocated for the SuperCluster system and expansion racks? |  |  |  |  |
| Does the floor layout meet the equipment maintenance access requirements: Rear maintenance: 36 in. (914 mm) Front maintenance: 48.5 in. (1232 mm) Top maintenance: 36 in. (914 mm) |  |  |  |  |
| Have cabinet stabilization measures been considered? |  |  |  |  |
| Does the raised floor satisfy the weight requirements for the new hardware? Shipping weight: Single-server SuperCluster M8, with three storage servers: 889 kg (1960 lbs) Single-server SuperCluster M8, with eleven storage servers: 1116 kg (2460 lbs) Dual-server SuperCluster M8, with six storage servers: 1153 kg (2541 lbs) Single-server SuperCluster M7, with three storage servers: 762 kg (1680 lbs) Single-server SuperCluster M7, with eleven storage servers: 975 kg (2150 lbs) Dual-server SuperCluster M7, with three storage servers: 975 kg (2150 lbs) Dual-server SuperCluster M7, with six storage servers: 1042 kg (2298 lbs) Expansion rack (quarter rack): EF: 431 kg (950 lbs) HC: 384 kg (848 lbs) Each additional storage server: EF: 28.1 kg (62 lbs) HC: 33.1 kg (73 lbs) Standard weight: Single-server SuperCluster M8, with three storage servers: 700 kg (1543 lbs) Single-server SuperCluster M8, with eleven storage servers: 927 kg (2043 lbs) Dual-server SuperCluster M8, with six storage servers: 963 kg (2124 lbs) Single-server SuperCluster M7, with three storage servers: 640 kg (1410 lbs) Single-server SuperCluster M7, with eleven storage servers: 855 kg (1886 lbs) Dual-server SuperCluster M7, with three storage servers: 828 kg (1824 lbs) Dual-server SuperCluster M7, with six storage servers: 894 kg (1971 lbs) Expansion rack (quarter rack): EF: 365 kg (804 lbs) HC: 384 kg (848 lbs) Each additional storage server: EF: 28.1 kg (62 lbs) HC: 33.1 kg (73 lbs) |  |  |  |  |
| Can floor tiles be removed without permission to accommodate service? |  |  |  |  |
| Are there cable routing channels or cutouts? |  |  |  |  |
| Are you providing any additional hardware? |  |  |  |  |
| Is the hardware you are providing fully compatible with the SuperCluster system? |  |  |  |  |
| Will the new hardware location require any non-standard cable lengths? |  |  |  |  |
| Is the floor to ceiling height a minimum of 2914 mm or 2.9 m (9.6 feet)? |  |  |  |  |
| Is the depth of the raised floor a minimum of 46 cm (18 inches)? |  |  |  |  |

# Data Center Environment Checklist

Complete the following checklist to ensure that the data center environment requirements are met. For information about environment requirements, see “Preparing the Site” in the installation guide that came with your system.

| Data Center Environment Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Does the computer room air handling meet temperature and humidity requirements? Refer to the installation guide for more information. |  |  |  |  |
| Does the installation floor layout satisfy the ventilation requirements? |  |  |  |  |
| Will the equipment be positioned so the exhaust air of one rack does not enter the air intake of another rack? |  |  |  |  |
| Are the perforated floor tiles each rated at 400 CFM or greater? |  |  |  |  |
| Do the data center air conditioners provide sufficient front to back airflow? Single-server SuperCluster M8, with three storage servers: 2,082 CFM (maximum) 1,658 CFM (typical) Single-server SuperCluster M8, with eleven storage servers: 2,852 CFM (maximum) 1,252 CFM (typical) Dual-server SuperCluster M8, with six storage servers: 3,773 CFM (maximum) 2,965 CFM (typical) Single-server SuperCluster M7, with three storage servers: 2,010 CFM (maximum) 1,400 CFM (typical) Single-server SuperCluster M7, with eleven storage servers: 2,642 CFM (maximum) 2,141 CFM (typical) Dual-server SuperCluster M7, with three storage servers: 3,369 CFM (maximum) 2,865 CFM (typical) Dual-server SuperCluster M7, with six storage servers: 3,605 CFM (maximum) 3,014 CFM (typical) Expansion rack (quarter rack): EF: 572 CFM (maximum) 401 CFM (typical) HC: 533 CFM (maximum) 373 CFM (typical) Each additional storage server: EF storage server: 94 CFM (maximum) 66 CFM (typical) HC storage server: 85 CFM (maximum) 59 CFM (typical |  |  |  |  |
| Is airflow adequate to prevent hot spots? |  |  |  |  |
| Can the data center continuously satisfy environmental requirements? Single-server SuperCluster M8, with three storage servers: 44,978 BTU/hour (maximum) 47,407 kJ/hour (maximum) 35,807 BTU/hour (typical) 37,740 kJ/hour (typical) Single-server SuperCluster M8, with eleven storage servers: 61,609 BTU/hour (maximum) 64,936 kJ/hour (maximum) 48,639 BTU/hour (typical) 51,265 kJ/hour (typical) Dual-server SuperCluster M8, with six storage servers: 81,505 BTU/hour (maximum) 85,906 kJ/hour (maximum) 64,034 BTU/hour (typical) 67,492 kJ/hour (typical) Single-server SuperCluster M7, with three storage servers: 43,416 BTU/hour (maximum) 45,780 kJ/hour (maximum) 30,238 BTU/hour (typical) 31,871 kJ/hour (typical) Single-server SuperCluster M7, with eleven storage servers: 57,064 BTU/hour (maximum) 60,145 kJ/hour (maximum) 46,241 BTU/hour (typical) 48,738 kJ/hour (typical) Dual-server SuperCluster M7, with three storage servers: 72,760 BTU/hour (maximum) 76,699 kJ/hour (maximum) 61,684 BTU/hour (typical) 65,015 kJ/hour (typical) Dual-server SuperCluster M7, with six storage servers: 77,878 BTU/hour (maximum) 82,083 kJ/hour (maximum) 65,103 BTU/hour (typical) 68,618 kJ/hour (typical) Expansion Rack Quarter Rack (EF): 12,362 BTU/hour (maximum) 13,042 kJ/hour (maximum) 8,654 BTU/hour (typical) 9,129 kJ/hour (typical) Expansion Rack Quarter Rack (HC): 11,516 BTU/hour (maximum) 12,149 kJ/hour (maximum) 8,064 BTU/hour (typical) 8,505 kJ/hour (typical) Each additional storage server (EF): 2,037 BTU/hour (maximum) 2,149 kJ/hour (maximum) 1,426 BTU/hour (typical) 1,504 kJ/hour (typical) Each additional storage server (HC): 1,825 BTU/hour (maximum) 1,926 kJ/hour (maximum) 1,278 BTU/hour (typical) 1,348 kJ/hour (typical) |  |  |  |  |
| Can more vented floor tiles be obtained if required? |  |  |  |  |

# Access Route Checklist

Complete the following checklist to ensure that the access route requirements are met.

| Access Route Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Has the access route been checked for clearances of the packaged equipment? |  |  |  |  |
| Do all the doors and entry ways conform to the width and height requirements for transportation, including the width of the unpacked unit: Height in shipping package: 85 in. (2159 mm) Width in shipping package: 48 in. (1219 mm) Height of SuperCluster M8 and expansion rack without shipping package: 78.74 in. (2000 mm) Height of SuperCluster M7 and expansion rack without shipping package: 78.66 in. (1998 mm) Width of rack without shipping package: 23.62 in. (600 mm) |  |  |  |  |
| Does the access route provide sufficient space for transport of the packed devices? |  |  |  |  |
| Are there any ramps or thresholds that are of concern? If yes, provide details. |  |  |  |  |
| Are there any stairs or ramps in the moving path for the new hardware? |  |  |  |  |
| Have you confirmed that all route incline angles are within the permitted range? |  |  |  |  |
| Have you confirmed that the access route is free of any obstacles that would expose the device to shock? |  |  |  |  |
| Are all the surfaces acceptable for rolling the new unpacked and packed equipment? |  |  |  |  |
| If a pallet jack is to be used, have you confirmed the following: The pallet jack supports the device weight? See “Data Center Room Checklist” on page 11 for the SuperCluster and expansion rack weights. The pallet jack tines are compatible with the shipping pallet? |  |  |  |  |
| If there are stairs, then is a loading elevator accessible for the equipment? |  |  |  |  |
| If an elevator is to be used, have you confirmed the following: The elevator car is wide enough for the system to be carried into it? The elevator car is high enough for the system to be carried into it? The load limit of the elevator is greater than the device weight? Are elevators available to handle the weight of the system provided earlier in this table? The elevator door meets the minimum height requirement of 86 inches for packaged rack delivery? |  |  |  |  |
| Does the path from the receiving location to the designated data center area support the weight of the unpacked equipment? |  |  |  |  |
| Is the path onto the raised floor rated for dynamic loading of the server? Refer to “Preparing the Site” in the Installation Guide for your SuperCluster system for requirements. |  |  |  |  |

# Facility Power Checklist

Complete the following checklist to ensure that the facility power requirements are met. For information about power requirements, refer to “Preparing the Site” in the installation guide for your SuperCluster system.

| Facility Power Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Do you know the required operating voltage and electric current level of the device and peripherals? |  |  |  |  |
| Will you be using single-phase (low-voltage or high-voltage) or three-phase (low-voltage or high-voltage) power? |  |  |  |  |
| Are enough power outlets provided within 2 meters for each rack? Options are: Low voltage, single-phase PDUs: 3 inputs/plugs per PDU, or 6 inputs/plugs total for system Low voltage, three-phase PDUs: 2 inputs/plugs per PDU, or 4 inputs/plugs total for system High voltage, single-phase PDUs: 3 inputs/plugs per PDU, or 6 inputs/plugs total for system High voltage, three-phase PDUs: 2 inputs/plugs per PDU, or 4 inputs/plugs total for system |  |  |  |  |
| Do the power outlets have appropriate socket receptacles for the PDU option ordered? Options are: Low-voltage 22 kVA single-phase High-voltage 22 kVA single-phase Low-voltage 25 kVA three-phase High-voltage 25 kVA three-phase |  |  |  |  |
| Will optional ground cables be attached to the rack? |  |  |  |  |
| Are the circuit breakers for the equipment suitable in terms of voltage and current-carrying capacities? |  |  |  |  |
| Does the power frequency meet the equipment specifications? |  |  |  |  |
| Are power outlets available for the new equipment at the designated location? |  |  |  |  |
| Will system power be delivered from two separate grids? |  |  |  |  |
| Is there a UPS to power the equipment? |  |  |  |  |
| Is the capacity of the UPS sufficient for the SuperCluster system? |  |  |  |  |
| Do you have the minimum required power sources to support the power load for the new hardware? Single-server SuperCluster M8, with three storage servers: Maximum: 12,523 W (13,182 VA) Typical: 9,969 W (10,494 VA) Single-server SuperCluster M8, with eleven storage servers: Maximum: 17,153 W (18,056 VA) Typical: 13,542 W (14,255 VA) Dual-server SuperCluster M8, with six storage servers: Maximum: 22,693 W (23,887 VA) Typical: 17,828 W (18,767 VA) Single-server SuperCluster M7, with three storage servers: Maximum: 12,088 W (12,724 VA) Typical: 8,419 W (8,862 VA) Single-server SuperCluster M7, with eleven storage servers: Maximum: 15,888 W (16,724 VA) Typical: 12,874 W (13,552 VA) Dual-server SuperCluster M7, with three storage servers: Maximum: 20,258 W (21,324 VA) Typical: 17,174 W (18,078 VA) Dual-server SuperCluster M7, with six storage servers: Maximum: 21,683 W (22,824 VA) Typical: 18,126 W (19,080 VA) Expansion rack, EF quarter rack: Maximum: 3.6 kW (3.7 kVA) Typical: 2.5 kW (2.6 kVA) Expansion rack, HC quarter rack: Maximum: 3.4 kW (3.4 kVA) Typical: 2.4 kW (2.4 kVA) Individual EF storage server: Maximum: .6 kW (.6 kVA) Typical: .4 kW (.4 kVA) Individual HC storage server: Maximum: .5 kW (.5 kVA) Typical: .4 kW (.4 kVA) |  |  |  |  |

# Safety Checklist

Complete the following checklist to ensure that the safety requirements are met. For information about safety, see “Preparing the Site” in the installation guide for your SuperCluster system.

| Safety Checklist Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Is there an emergency power shut off? |  |  |  |  |
| Is there a fire protection system in the data center room? |  |  |  |  |
| Is the computer room adequately equipped to extinguish a fire? |  |  |  |  |
| Is antistatic flooring installed? |  |  |  |  |
| Is the floor below the raised floor free of obstacles and blockages? |  |  |  |  |

# Logistics Checklist

Complete the following checklist to ensure that the logistics requirements are met. For information about unpacking and space requirements, see “Preparing the Site” in the installation guide for your SuperCluster system.

| Logistics Checklist Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Do you have contact information for the data center personnel? |  |  |  |  |
| Is there security or access control for the data center? |  |  |  |  |
| Are there any security background checks or security clearances required for vendor personnel to access the data center? If yes, do you have a recommended agency? |  |  |  |  |
| How many days in advance must background checks be completed? |  |  |  |  |
| Are there any additional security access issues? |  |  |  |  |
| Is computer room access available for installation personnel? |  |  |  |  |
| Are laptops, cell phones, and cameras allowed in the data center? |  |  |  |  |
| Does the building have a delivery dock? |  |  |  |  |
| Is there a delivery/unpacking/staging area? |  |  |  |  |
| Is the delivery inside? |  |  |  |  |
| If the delivery is not inside, then is the site prepared for uncrating? |  |  |  |  |
| Is the unpacking/staging area protected from the elements? |  |  |  |  |
| Does the building have adequate receiving space? |  |  |  |  |
| Is the unpacking area air-conditioned to avoid thermal shock for various hardware components? |  |  |  |  |
| Will sufficient moving personnel be available to install the hardware? |  |  |  |  |
| Is union labor required for any part of the delivery or installation? |  |  |  |  |
| Are you prepared for uncrating and trash removal? |  |  |  |  |
| Is uncrating of cabinet and cabinet trash removal required? |  |  |  |  |
| Are there any restrictions on delivery truck length, width, or height? |  |  |  |  |
| Does the customer allow cardboard boxes and other packing material in the computer room? If no, do ground-level deliveries require a truck with a side rail lift? |  |  |  |  |
| Is there a time constraint on dock access? If yes, provide time constraints. |  |  |  |  |
| Is tail lift required on delivery carrier to unload the equipment at the delivery dock? |  |  |  |  |
| Will any of the following be required to place equipment in computer room? Stair walkers Lifters Ramps Steel plates Floor covers |  |  |  |  |
| Does the delivery carrier require any special equipment, such as nonfloor damaging rollers, transport dollies, pallet jacks or fork lifts? |  |  |  |  |

# Network Configuration Checklist

Complete the following checklist to ensure that the network configuration requirements are met for the following networks in the SuperCluster system:

IB network: Used for communication between components installed in the SuperCluster system

Client access network: 10GbE network, with connections to the 10GbE network interface cards in the compute servers

Oracle ILOM management network: Oracle ILOM network, with connections to the Oracle ILOM (NET MGT) port on the compute servers, storage servers and ZFS storage appliance

Host management network: 1GbE network, with connections to the NET 0 to 3 ports on the 1GbE NICs in the compute servers, and the NET 0 port to the storage servers and ZFS storage appliance

For information about IP addresses, see “Understanding the Network Requirements” in the overview guide for your SuperCluster system.

| Network Specification Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Were any conflicts found while running the checkip.sh script before connecting the network? See “Understanding the Network Requirements” in the overview guide for your SuperCluster system for information on the script. |  |  |  |  |
| Were any conflicts found while running the checkip.sh script after initial configuration? See “Understanding the Network Requirements” in the overview guide for your SuperCluster system for information on the script. |  |  |  |  |
| Do you have the appropriate number of network drops available for the SuperCluster system? 10GbE client access network: 2 network drops for every 10GbE NIC installed in the compute servers 1GbE management network: 1 network drop that connects to the Ethernet management switch |  |  |  |  |
| Did you run the required network cables from your network equipment to the location where the system will be installed? |  |  |  |  |
| Did you label the network cables that will connect to the system? |  |  |  |  |
| Do you have suitable transceivers for the 10GbE switch at your site? Note that each 10GbE NIC installed in the SuperCluster M7 comes with pre-installed transceivers, so additional transceivers are not needed for those 10GbE NICs. |  |  |  |  |
| Will the Ethernet management switch have IP routing disabled? |  |  |  |  |
| Do you have the appropriate number of IP addresses reserved for the system? See the configuration worksheets for your SuperCluster system for more information. |  |  |  |  |

# Database High Availability Checklist

Complete the following checklist to ensure the requirements for high availability are met for SuperCluster system. For additional information about high availability, refer to the Oracle Database High Availability Overview.

| Database High Availability Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Have high redundancy disk groups been configured for best protection against different storage failures and corruptions? |  |  |  |  |
| Will the pre-optimized and configured database be used after deployment? |  |  |  |  |
| Have you reviewed the Oracle Exadata Storage Server Software patching overview and patch testing guidelines in My Oracle Support note 1262380.1? |  |  |  | - |
| Have you reviewed the Oracle Exadata Storage Server Software Maximum Availability Architecture (MAA) web site for post-deployment steps to achieve MAA? The web site is available at http://www.oracle.com/goto/maa |  |  |  |  |

# Storage Server Storage Capacity Checklist

Complete the checklist in this section to determine if the amount of storage in the storage servers in the SuperCluster system or expansion rack is sufficient for your needs. The following tables provide the amount of storage available in each type of rack, depending on ASM normal or high redundancy.

The Oracle X7-2L Exadata Storage Servers are supported for SuperCluster M8. The Oracle X6-2L Exadata Storage Servers and Oracle X5-2L Exadata Storage Servers are supported for SuperCluster M7. Following are the characteristics of the storage servers:

The storage servers are available with either Extreme Flash or High Capacity storage.

SuperCluster M8 and SuperCluster M7 comes with a minimum of three storage servers. From three (dual-server configuration) to eight (single-server configuration) additional storage servers can be added to the system.

The expansion rack is available as a quarter rack, with four storage servers. You can increase the number of storage servers in the expansion rack up to a maximum of 18 storage servers.

Refer to the Oracle Exadata Storage Server Software User's Guide for information about maximum availability. Also see the following tables for more information on storage capacities based on the level of redundancy that you choose.

Note – The tables do not include capacities of the PCIe flash cards that are part of the HC storage server infrastructure.

Table 1: X7-2L Single Storage Server Capacities

| Capacity Type | 8 x 6.4-TB Extreme Flash Drives | 12 x 10-TB High Capacity Drives |
| --- | --- | --- |
| Raw PCI flash capacity | 51.2 TB | 120 TB |
| Usable mirrored capacity (ASM normal redundancy) | 20 TB | 50 TB |
| Usable triple mirrored capacity (ASM high redundancy) | 17.2 TB | 37.5 TB |

Table 2: X6-2L Single Storage Server Capacities

| Capacity Type | 8 x 3.2-TB Extreme Flash Drives | 12 x 8-TB High Capacity Drives |
| --- | --- | --- |
| Raw PCI flash capacity | 25.6 TB | 96 TB |
| Usable mirrored capacity (ASM normal redundancy) | 10 TB | 40 TB |
| Usable triple mirrored capacity (ASM high redundancy) | 8.6 TB | 30 TB |

Table 3: X5-2L Single Storage Server Capacities

| Capacity Type | 8 x 1.6-TB Extreme Flash Drives | 12 x 8-TB High Capacity Drives |
| --- | --- | --- |
| Raw PCI flash capacity | 12.8 TB | 96 TB |
| Usable mirrored capacity (ASM normal redundancy) | 5 TB | 40 TB |
| Usable triple mirrored capacity (ASM high redundancy) | 4.3 TB | 30 TB |

| Exadata Storage Server Storage Capacity Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Does the SuperCluster system have the storage capacity that you need for the storage servers? |  |  |  |  |
| Does the expansion rack have the storage capacity that you need for the storage servers? |  |  |  |  |

# Auto Service Request Checklist

Complete the following checklist if you are planning to use Auto Service Request with the SuperCluster system. For additional information about Auto Service Request, see “Maintaining the System” in the administration guide for your SuperCluster system.

| ASR Service Request Considerations | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Do you have a My Oracle Support to register Auto Service Request? |  |  |  |  |
| Do you have your Oracle Support Customer Support Identifier (CSI) number? |  |  |  |  |
| Will you be using a standalone server for the ASR Manager? If yes, you must have the standalone server available before the Oracle installers arrive on site. |  |  |  |  |
| Do you have the host name and IP address for the server that will have ASR Manager? |  |  |  |  |
| Will the system need a proxy server? If so, what is the host name and IP address for the proxy server? |  |  |  |  |
| Do you have the technical contact information for ASR? This information should include the first name, last name, and email address of the contact. |  |  |  |  |
| Do you have Oracle Auto Service Request Release 3.5 or later? If not, go to http://www.oracle.com/asr and click on the Downloads link to download the latest version. |  |  |  |  |

# Oracle Enterprise Manager Ops Center Checklist

For previous versions of Oracle Enterprise Manager Ops Center, the Ops Center software was installed and run from the SuperCluster system. Beginning with the Oracle Enterprise Manager Ops Center 12c Release 2 (12.2.0.0.0) release, the Ops Center software must now run on a system outside of the SuperCluster system.

Complete the following checklist to verify that the external system that will be running the Oracle Enterprise Manager Ops Center meets the necessary requirements before your SuperCluster system is delivered to your site.

For all entries that are not yes or no questions, enter your answers in the Comment column.

| Oracle Enterprise Manager Ops Center Requirements | Yes | No | N/A | Comment |
| --- | --- | --- | --- | --- |
| Have you identified a virtual machine or physical server outside of the SuperCluster system to host Ops Center Enterprise Controller? |  |  |  |  |
| Did you receive the ops_center_preflight_check-versionnum.bin script from Oracle, and did you perform the following: Did you run that script on the system that you will be using as the Enterprise Controller host? Note that this script must be run as the root user. If the Enterprise Controller is set up in a High Availability configuration, did you run that script on both systems as the root user? Note that the High Availability installation is not automated. Did you send the output back to Oracle prior to the SuperCluster system being shipped to you? |  |  |  |  |
| Is the external system that will run Ops Center an x86 (64-bit) or SPARC (64-bit) system? Note that the system must be running the Oracle Solaris 11 OS. |  |  |  |  |
| Does your Enterprise Controller host meet the necessary CPU requirements: Modern 2 Ghz+ CPU (for SPARC systems, SPARC T4 or later) At least 4 cores for the first SuperCluster system 1 additional CPU core for every additional SuperCluster system |  |  |  |  |
| Does your Enterprise Controller host meet the necessary memory requirements: 16 GB of RAM for the first SuperCluster system Additional 2 GB of RAM for every additional SuperCluster system |  |  |  |  |
| Does your Enterprise Controller host meet the necessary disk requirements: Two disks in a mirrored configuration, with at least 446 GB of available storage each A single rpool, with: An additional rpool/eclibs file system mounted as /eclibs An additional rpool/u01 file system mounted as /u01 The following disk space on both mirrored disks: In the active and running boot environment: 85 GB for the /var file system (EC/PC runtime) 30 GB for the / file system (EC/PC installation and data) 240 GB for the /u01 file system On the rpool/eclibs file system (mounted as /eclibs): 15 GB for the /eclibs/eclib file system (EC library) 45 GB for the /eclibs/s11repo file system (IPS repository) 15 GB for the /eclibs/1x_s8-10repo file system (Linux and Solaris 8-10 library) At least 16 GB for swap space. If you add additional assets, you should increase the swap space by 2 GB for each additional SuperCluster system. |  |  |  |  |
| Does your Enterprise Controller host meet the necessary network requirements: Are the required ports and protocols allowed to pass through the network between the Enterprise Controller host and the SuperCluster system? For more information, refer to the Oracle Enterprise Manager Ops Center Ports and Protocols 12c Release 2 (12.2.0.0.0) document, located at: http://docs.oracle.com/cd/E40871_01/doc.122/e51942/toc.htm Have you verified that the network where the SuperCluster system is located is fully accessible from the Enterprise Controller host? Have you verified that the round-trip time (ping) from the Enterprise Controller host to the SuperCluster management network is within acceptable parameters: The ideal ping time should be 50 ms or less. A ping time between 50 ms and 75 ms is acceptable, though performance will be slow. A ping time over 75 ms is not within the acceptable parameters. |  |  |  |  |
| Does your Enterprise Controller host meet the necessary software requirements: Oracle Solaris 11 SRU 14.5 OS. Enterprise Controller host can not contain any nonglobal zones. |  |  |  |  |
| If you plan to manage multiple SuperCluster systems from a single Ops Center, have you planned ahead for nonoverlapping networks during the planning phase? Multiple engineered system instances can be discovered and managed by a single Ops Center, provided that none of the engineered system instances have overlapping networks (networks that have the same Classless Inter-Domain Routing [CIDR], or are subblocks of the same CIDRs, such as 192.168.0.0/21 and 192.168.0.0/24, which are overlapping). This condition must be met, regardless of the underlying fabric (InfiniBand, EoIB, or Ethernet). In addition, verify that there is no other network defined in Ops Center that overlaps with any of the networks of any of the engineered system instances that you want to manage. For more information, refer to the Oracle Enterprise Manager Ops Center Feature Reference Guide 12c Release 2 (12.2.0.0.0) document, specifically the section “Configuring Oracle Engineered Systems” in the chapter “Oracle Engineered Systems,” located at: http://docs.oracle.com/cd/E40871_01/doc.122/e38539/engineered_systems.htm#sthref3042 |  |  |  |  |

# Footnotes

For raw capacity, 1 GB = 1 billion bytes. Capacity calculated using normal space terminology of 1 TB = 1024 * 1024 * 1024 * 1024 bytes. Actual formatted capacity is less.

For raw capacity, 1 GB = 1 billion bytes. Capacity calculated using normal space terminology of 1 TB = 1024 * 1024 * 1024 * 1024 bytes. Actual formatted capacity is less.

For raw capacity, 1 GB = 1 billion bytes. Capacity calculated using normal space terminology of 1 TB = 1024 * 1024 * 1024 * 1024 bytes. Actual formatted capacity is less.