## Title Page
Oracle® Communications
HP Gen9 C-Class Platform
Assembly Instructions
E65488-01 Revision 01
2015-09-15

## Oracle Copyright
Oracle® Communications HP Gen9 C-Class Platform Assembly Instructions
Copyright © 2013,2015 Oracle and/or its affiliates. All rights reserved.
This software and related documentation are provided under a license agreement containing restrictions on use and disclosure and are protected by intellectual property laws. Except as expressly permitted in your license agreement or allowed by law, you may not use, copy, reproduce, translate, broadcast, modify, license, transmit, distribute, exhibit, perform, publish, or display any part, in any form, or by any means. Reverse engineering, disassembly, or decompilation of this software, unless required by law for interoperability, is prohibited. The information contained herein is subject to change without notice and is not warranted to be error-free. If you find any errors, please report them to us in writing. If this is software or related documentation that is delivered to the U.S. Government or anyone licensing it on behalf of the U.S. Government, then the following notice is applicable: U.S. GOVERNMENT END USERS: Oracle programs, including any operating system, integrated software, any programs installed on the hardware, and/or documentation, delivered to U.S. Government end users are "commercial computer software" pursuant to the applicable Federal Acquisition Regulation and agency-specific supplemental regulations. As such, use, duplication, disclosure, modification, and adaptation of the programs, including any operating system, integrated software, any programs installed on the hardware, and/or documentation, shall be subject to license terms and license restrictions applicable to the programs. No other rights are granted to the U.S. Government. This software or hardware is developed for general use in a variety of information management applications. It is not developed or intended for use in any inherently dangerous applications, including applications that may create a risk of personal injury. If you use this software or hardware in dangerous applications, then you shall be responsible to take all appropriate fail-safe, backup, redundancy, and other measures to ensure its safe use. Oracle Corporation and its affiliates disclaim any liability for any damages caused by use of this software or hardware in dangerous applications. Oracle and Java are registered trademarks of Oracle and/or its affiliates. Other names may be trademarks of their respective owners. Intel and Intel Xeon are trademarks or registered trademarks of Intel Corporation. All SPARC trademarks are used under license and are trademarks or registered trademarks of SPARC International, Inc. AMD, Opteron, the AMD logo, and the AMD Opteron logo are trademarks or registered trademarks of Advanced Micro Devices. UNIX is a registered trademark of The Open Group. This software or hardware and documentation may provide access to or information about content, products, and services from third parties. Oracle Corporation and its affiliates are not responsible for and expressly disclaim all warranties of any kind with respect to third-party content, products, and services unless otherwise set forth in an applicable agreement between you and Oracle. Oracle Corporation and its affiliates will not be responsible for any loss, costs, or damages incurred due to your access to or use of third-party content, products, or services, except as set forth in an applicable agreement between you and Oracle.

## Doc Inst.
Locate Product Documentation on the Oracle Help Center
Oracle customer documentation is available on the web at the Oracle Help Center (formerly known as OTN) site,
http://docs.oracle.com/en/industries/communications/
You do not have to register to access these documents. Viewing some of these documents may require Adobe
Acrobat Reader, which can be downloaded at:
http://www.adobe.com
1. Access the Oracle Help Center site at:
http://docs.oracle.com/en/industries/communications
2. This link will take you directly to the Oracle Communications industry page.
3. Navigate to your Product and click. This will take you to the available Releases page.
4. Click on the applicable Product release to open the media pack.
5. Click on the desired document to download.

## Reference
REFERENCE TAB
REFERENCE LIST
1 | 7309260 | SYSTEM INTERCONNECT, GEN9, DATA, TOPOLOGIES 1-8, C-CLASS AND RMS, Latest Rev
2 | TR007537 | TECHNICAL REFERENCE, GEN9 SYSTEM, NETWORK TOPOLOGIES, C-CLASS AND RMS, Latest Rev
3 | 892-0125-01 | SYSTEM INTERCONNECT_AC POWER_C CLASS, Latest Rev

## Purpose
Purpose and Scope
The following worksheets provide information to support assembly of c-class systems using HP Gen9 servers and blades for OCDSR, OCUDR and OCPM. The intent of this document is to define the installation details and assist the customer or their agent in installing the Gen9 systems in a cabinet with all Gen9 servers and blades or co-located with DL360/DL380 Gen8 Servers and Blades. The customer will be responsible for ordering the servers and blades to support the application being deployed. This may include the customer ordering the cabinet from Oracle or providing their own cabinet for installation of the new Gen9 hardware .The Gen9 Hardware from HP requires a cabinet that meets EIA-310 D Type A per section 4.1.1. The 870-3103-01 is a Wright Line Specific cabinet and may be provided by the customer to support the HP Gen9 servers and blades. The HP Gen9 servers and blades may be required to support expansion of existing systems then this document will assist in how to install the new Gen9 hardware in an existing cabinet assembly.
AC Cabinet
Cabinet layout for the hardware solution on HP c-Class hardware
FIGURE 1A: SINGLE PHASE 870-3111-01 CABINET WITH (3) Encl, (GEN9 1x2U SERVER/ 2 DL360 GEN9)
FIGURE 1B: SINGLE PHASE 870-3111-01 CABINET WITH (2) Encl, (GEN9 6x2U SERVERS/ 12 DL360 GEN9)
FIGURE 1C: SINGLE PHASE 870-3111-01 CABINET WITH (1) Encl, (GEN9 11x2U SERVERS/ 12 DL360 GEN9)
FIGURE 1D: THREE PHASE 870-3111-01 CABINET WITH (3) Encl, (GEN9 1x2U SERVER/ 2 DL360 GEN9)
FIGURE 1E: THREE PHASE 870-3111-01 CABINET WITH (2) Encl, (GEN9 6x2U SERVERS/ 12 DL360 GEN9)
FIGURE 1F: THREE PHASE 870-3111-01 CABINET WITH(1) Encl, (GEN9 11x2U SERVERS/ 12 DL360 GEN9)
FIGURE 1G: Comingled GEN8 and GEN9 Server with Single Phase Pwr and (3) Encl, (1x2U SERVER/ 2 DL360)
FIGURE 1H: Comingled GEN8 and GEN9 Server with Single Phase Pwr and (2) Encl, (6x2U SERVERS/ 12 DL360)
FIGURE 1J: Comingled GEN8 and GEN9 Server with Single Phase Pwr and (1) Encl, (11x2U SERVERS/ 12 DL360)
FIGURE 1K: Comingled GEN8 and GEN9 Server with Three Phase Power and (3) Encl, (1x2U SERVER/ 2 DL360)
FIGURE 1L: Comingled GEN8 and GEN9 Server with Three Phase Power and (2) Encl, (6x2U SERVERS/ 12 DL360)
FIGURE 1M: Comingled GEN8 and GEN9 Server with Three Phase Power and (1) Encl, (11x2U SERVERS/ 12 DL360)
The Following Figures support the Wright Line Cabinet:
FIGURE 1N: 870-3103-01 in the 805-0585-01 WRIGHT LINE CABINET (44U) WITH GEN9 SERVERS AND BLADES
FIGURE 1P: 870-3103-01 in the 805-0583-01 WRIGHT LINE CABINET (40U) WITH GEN9 SERVERS AND BLADES
FIGURE 1R: 870-3103-01 in the 805-0582-01 WRIGHT LINE CABINET (44U) ) WITH GEN9 SERVERS AND BLADES
FIGURE 1S: 870-3103-01 in the 805-0562-01 WRIGHT LINE CABINET (40U) WITH GEN9 SERVERS AND BLADES
FIGURE 1T: 870-3103-01 in the 805-0585-01 WRIGHT LINE CABINET (44U) COMINGLED WITH GEN9 AND GEN8 SERVERS AND BLADES
FIGURE 1W: 870-3103-01 in the 805-0583-01 WRIGHT LINE CABINET (40U)COMINGLED WITH GEN9 AND GEN8 SERVERS AND BLADES
FIGURE 1X: 870-3103-01 in the 805-0582-01 WRIGHT LINE CABINET (44U) COMINGLED WITH GEN9 AND GEN8 SERVERS AND BLADES
FIGURE 1Y: 870-3103-01 in the 805-0562-01 WRIGHT LINE CABINET (40U) COMINGLED WITH GEN9 AND GEN8 SERVERS AND BLADES
c-Class item picklist
This is a list of all the hardware item numbers that are available for the Eagle XG c-Class program. This information is For Reference Only.
TABLE A1 : 870-3111-01 C-CLASS EAGLE XG HARDWARE PART NUMBERS
TABLE A2: 870-3103-01 C-CLASS_AC_WRIGHT LINE CABINET HARDWARE PART NUMBERS
AC Cabinet Assembly Notes
Assembly Notes to support the hardware solution on HP c-Class hardware.
870-3111-01_Cab Assy_Details
FIGURE 2: Cabinet Mounting Rails and Mounting Hardware
FIGURE 3: Panduit Air Duct and CISCO 4948E-F SWITCH MOUNTED VIEW
FIGURE 4: Panduit Air Duct and CISCO 4948E-F Switch Mounting Detail
FIGURE 5: HP C7000 ENCLOSURE GEN9 CABINET ASSY VIEWS SHOWN INSTALLED IN HP CABINET
870-3103-01_Cab Assy_Details
FIGURE 10: Panduit Air Duct (CDE2) and CISCO 4948E-F SWITCH
FIGURE 11: Panduit Air Duct and CISCO 4948E-F SWITCH MOUNTING DETAIL
FIGURE 12: TYPICAL CAGE NUT INSTALLATION DETAIL IN A CABINET WITH SQUARE HOLES
FIGURE 13: TYPICAL MOUNTING DETAIL DL380 GEN9 SERVER IN A CABINET WITH SQUARE HOLES
FIGURE 14: INSTALLING A c7000 ENCLOSURE INTO A WRIGHT LINE CABINET
Cable Routing
FIGURE 15: DATA CABLE ROUTING
870-3111-01 Component Labeling
Views for cabinets and the component names
FIGURE 20 : SINGLE PHASE PDU LABELING
FIGURE 21 : THREE PHASE PDU LABELING
FIGURE 22 : EXTENSION BAR LABELING
FIGURE 23 : CABLE LABELING
FIGURE 24 : FRONT DOOR LABELING
FIGURE 25 : CONSOLIDATED LABEL FOR CABINET
FIGURE 26 : CABINET LABEL 7300465
FIGURE 27: CABINET LABELING -DL380 GEN9 SERVERS FRONT RAIL
FIGURE 28: CABINET LABELING -DL360 GEN9 SERVERS FRONT RAIL
FIGURE 29: CABINET LABELING -TYPICAL SERVERS LABELING REAR RAIL
FIGURE 30: CABINET LABELING 4948E-F SWITCHES- FRONT RAIL
FIGURE 31: CABINET LABELING 4948E-F SWITCHES- REAR RAIL
870-3111-01 Component Labeling
Views for cabinets and the component names
FIGURE 32: PDU LABELING
FIGURE 33 : CABLE LABELING FOR C7000 ENCLSOURE
FIGURE 34: CABLE LABELING FOR SERVERS
FIGURE 35 : FRONT DOOR LABELING
FIGURE 36: CONSOLIDATED LABEL DETAILS
FIGURE 37: 1U AND/OR 2U SERVER AND SWITCH DESIGNATIONS 44U WRIGHT LINE CABINET WITH (1) c7000 ENCL
FIGURE 38: 1U AND/OR 2U SERVER AND SWITCH DESIGNATIONS 40U WRIGHT LINE CABINET WITH (1) c7000 ENCL
FIGURE 39: 1U AND/OR 2U SERVER AND SWITCH DESIGNATIONS 44U WRIGHT LINE CABINET WITH (2) c7000 ENCL
FIGURE 40: 1U AND/OR 2U SERVER AND SWITCH DESIGNATIONS 40U WRIGHT LINE CABINET WITH (2) c7000 ENCL
FIGURE 41: CABINET LABEL
FIGURE 42: CABINET LABELING -DL380 GEN9 SERVERS FRONT RAIL
FIGURE 43: CABINET LABELING -TYPICAL SERVERS LABELING REAR RAIL
FIGURE 44: CABINET LABELING 4948E-F SWITCHES- FRONT RAIL
FIGURE 45: CABINET LABELING 4948E-F SWITCHES- REAR RAIL
870-3111-01 Power Cables
From/To routing of power cables
TABLE B: SINGLE PHASE POWER CABLES - EAGLE XG CABINET WITH (3) ENCL/(2) CISCO 4948E-F, (1) DL380 OR (2) DL360
TABLE C: SINGLE PHASE POWER CABLES - EAGLE XG CABINET WITH (1) OR (2) ENCL, (2) CISCO 4948E-F, UP TO(12) RMS
TABLE D: THREE PHASE POWER CABLES - EAGLE XG CABINET WITH(3) ENCL,(2)CISCO 4948E-F, (1) DL380 OR (2) DL360
TABLE E: THREE PHASE POWER CABLES - EAGLE XG CABINET WITH (1) OR (2) ENCL, (2) CISCO 4948E-F, UP TO (12) RMS
870-3103-01 Power Cables
From/To routing of power cables
TABLE K: POWER CABLES for use with Wright Line PDU 17110314 50 AMP PDU
TABLE L: POWER CABLES 30 AMP PDU
TABLE M: POWER CABLES for use with Wright Line PDU VZIAN21650IPB 50 AMP PDU
870-3111-01_Power Tables
TABLE F: SINGLE PHASE NA/JAPAN CABINET (EXGXX) POWER CONSUMPTION WITH HP RMS
TABLE G: SINGLE PHASE INTERNATIONAL CABINET (EXGXX) POWER CONSUMPTION WITH HP RMS
TABLE H: THREE PHASE NA/JAPAN CABINET (EXGXX) POWER CONSUMPTION WITH HP RMS
TABLE J: THREE PHASE INTERNATIONAL CABINET (EXGXX) POWER CONSUMPTION WITH HP RMS
870-3103-01_Power Tables
TABLE N: 50 amp -3 Phase Delta Monitored PDU
TABLE P: 30 amp -3 Phase Delta Monitored PDU
TABLE R: 50 amp -3 Phase Delta Monitored PDU
Cabinet Footprint
FIGURE 50: CABINET FOOTPRINT for 870-3111-01
FIGURE 52: Cabinet Footprint for Wright Line cabinets with TOC 870-3103-01
FIGURE 53: Cabinet Footprint for Wright Line cabinets without TOC 870-3103-01
Transit Bracket Installation
FIGURE 55: INSTALLATION OF TRANSIT BRACKETS FOR 870-3111-01
PURPOSE TAB

## 870-3111-01 ITEM PICKLIST
870-3111-01 ITEM PICKLIST TAB
TABLE A1: 870-3111-01 C-CLASS HP CABINET WITH HARDWARE PART NUMBERS (FOR REFERENCE ONLY)
ORACLE P/N | HP OR MANUFACTURES P/N | QTY | DESCRIPTION Oracle Bill of Materials shall be used. The part numbers shown below may not be the latest configuration and are shown for reference only.
CABINET HARDWARE
805-0614-01 | BW904A | 1 | HP BW904A_642 1075MM_SHOCK INTELLIGENT SERIES RACK_ROHS
805-0614-02 | BW926A | 1 | HP BW926A_600MM_RACK TIE DOWN KIT_ROHS
805-0614-03 | BW906A | 1 | HP BW906A_42U 1075MM_SIDE PANEL KIT_ROHS
805-0614-04 | BW932A | 1 | HP BW932A_600MM_JB_RACK STABILIZER KIT_ROHS
805-0614-05 | BW891A | 1 | HP BW891A_INTELLIGENT SERIES RACK GROUNDING KIT_ROHS
805-0614-06 | BW930A | 1 | HP BW930A_AIRFLOW OPTIMIZATION KIT_ROHS
804-2085-G01 | BW929A | AR | HP 1U_FILLER PANEL_UNIVERSAL_100/PKG
TR007522 | PROCESS DOC | 0 | TR_ASSY INSTRUCTIONS_GEN9 C-CLASS PLATFORM_AC_C-CLASS SYSTEM
892-0125-01 | PROCESS DOC | 0 | SYSTEM INTERCONNECT_AC POWER_C CLASS
NETWORK HARDWARE - CISCO AGGREGATION SWITCHES
805-0592-02 | SEE RELEASED SPECIFICATION | AR | CISCO 4948E-F_AC_48 PORT ETHERNET SWITCH_002_ROHS 5/6
805-0593-01 | PANDUIT PN CDE2 | AR | PANDUIT CDE2_MODULAR SWITCH INLET DUCT_ROHS (FOR USE WITH 805-0592-02)
SFP MODULES FOR 4948 SERIES SWITCHES
805-0191-R01 | CISCO PN GLC-SX-MM= | AR | 1000BASE-SX_SFP FIBER OPTIC TRANSCEIVER_ROHS 5/6
805-0191-R02 | CISCO PN GLC-LH-SM= | AR | 1000BASE-LX/LH_SFP FIBER OPTIC TRANSCEIVER_ROHS 5/6
805-0191-R03 | CISCO PN SFP-10G-SR= | AR | 10G BASE-SR MULTIMODE SFP FIBER OPTIC TRANSCEIVER_ROHS 5/6
805-0191-R04 | CISCO PN SFP-10G-LR= | AR | 10G BASE-LR SINGLEMODE SFP FIBER OPTIC TRANSCEIVER_ROHS 5/6
GEN9 SERVERS
NA | SEE TR007457 | AR | DL380 GEN9_AC_SERVER
NORTH AMERICA INPUT POWER OPTIONS (PICK 2 OF THE SAME TYPE PER ENCLOSURE)
804-2062-G07 | 252663-D75 | AR | HP 252663-D75_PDU_200-240V_40A_CS8265C-50A_NO EXTENSION BARS_ROHS
804-2062-G10 | AF519A | AR | HP AF519A_PDU_208V-3 PHASE_CS8365C-69A_ROHS (NA/JAPAN)
804-2987-G01 | AF500A | AR | PDU EXTENSION BAR KIT (2 EXT BARS PER KIT) SEE NOTE 1
INTERNATIONAL INPUT POWER OPTIONS (PICK 2 OF THE SAME TYPE PER ENCLOSURE)
804-2062-G04 | 252663-B33 | AR | HP 252663-B33_PDU_200-240V_32A_IEC 309-32A_NO EXTENSION BARS_ROHS
804-2062-G11 | AF518A | AR | HP AF518A_PDU_380-415V-3 PHASE_IEC 309-32A_ROHS (INTERNATIONAL)
804-2987-G01 | AF500A | AR | PDU EXTENSION BAR KIT (2 EXT BARS PER KIT) SEE NOTE 1
c7000 ENCLOSURE
805-0540-GXX | BOM | AR | C7000_AC_BLADE ENCLOSURE_003_ROHS
805-0189-G01 | 516733-B21 | AR | 516733-B21_PROCURVE 6120XG_10 GBE_C7000 ENCLOSURE SWITCH_001_ROHS (PICK IN PAIRS; MAX 6)
805-0190-G01 | 406740-B21 | AR | HP-406740-B21_1GBE_PASS THRU MODULE_001_ROHS
805-0627-01 | 658247-B21 | AR | HP 658247-B21_BLADE SWITCH_C-CLASS_HP6125G_1GB_ROHS
7093049 | 711307-B21 | AR | 711307-B21_BLADE SWITCH, 10GBE, HP 6125XLG
SFP MODULES FOR 805-0189-G01 PROCURVE 6120XG SWITCH
805-0567-G01 | 453154-B21 | AR | 453154-B21_1000BASE-T_SFP COPPER TRANSCEIVER_ROHS
805-0567-G02 | 453151-B21 | AR | 453151-B21_1000BASE-SX_MULTIMODE SFP FIBER OPTIC TRANSCEIVER_ROHS
805-0567-G03 | 455883-B21 | AR | 455883-B21_10GBASE-SR_MULTIMODE SFP FIBER OPTIC TRANSCEIVER_ROHS
805-0567-G04 | 455886-B21 | AR | 455886-B21_10GBASE-LR_SINGLEMODE SFP FIBER OPTIC TRANSCEIVER_ROHS
805-0567-G05 | 455889-B21 | AR | 455889-B21_10GBASE-LRM_MULTIMODE SFP FIBER OPTIC TRANSCEIVER_ROHS
SFP MODULES FOR 805-0627-01 6125G SWITCH
805-0628-01 | JD089B | AR | JD089B_HP_X120_SFP RJ45 T TRANSCEIVER_ROHS 5/6
SFP MODULES FOR 7093053 6125XLG SWITCH
805-0628-01 | JD089B | AR | JD089B_HP_X120_SFP RJ45 T TRANSCEIVER_ROHS 5/6
7093055 | JD092B | AR | JD092B_SFP+ TRANSCEIVER, 10GBE, HP X130 LC SR 850NM
HALF HEIGHT BLADE OPTIONS
NA | SEE TR007457 | AR | BL460 GEN9_AC_SERVER BLADE
STORAGE BLADE OPTIONS
805-0619-01 | BOM |  | HP_STORAGE BLADE_146GB HARD DRIVES_ROHS
805-0619-02 | BOM |  | HP AP882A_STORAGE BLADE_600GB HARD DRIVES_ROHS
805-0619-03 | BOM |  | HP_STORAGE BLADE_146GB HARD DRIVES_ROHS
805-0619-04 | BOM |  | HP_STORAGE BLADE QW918A_600GB HARD DRIVES_ROHS
INSTALLATION MATERIAL
7306951 | BOM | AR | ASSEMBLY MATERIALS_TWO SWITCHES_AC POWER CABLES_CABLE MGMT BARS_ROHS 5/6
814-0034-07 | BOM | AR | ASSEMBLY MATERIALS_RMS_EXTENTION KIT_ETH CABLES_ROHS 5/6
7098565 | BOM | AR | ASSEMBLY MATERIALS, ETHERNET CABLES, C-CLASS ENCLOSURE (SUPERSEDES 814-0034-08)
7300465 | LABEL | AR | LABEL SHEET, FRAME AND COMPONENT IDENTIFICATION
805-0560-G08 | SEE RELEASED SPECIFICATION 805-0560-G08 | AR | FIBER CABLE_1 METER_MULTI-MODE_008_ROHS
658-1158-XX | SEE RELEASED SPECIFICATION 658-1158-XX | AR | GEN_DWG_LABEL_FRAME ID_EXG-XX (EXG-00 THROUGH EXG-06)
804-2181-01 | HP PN 408375-001 | AR | 408375-001_BL C7000 CHASSIS DEVICE BAY DIVIDER_FOR HALF HEIGHT BLADES_ROHS
804-2085-G01 | HP PN BW929A | AR | HP 1U_FILLER PANEL_UNIVERSAL_100/PKG
FLOOR MOUNTING KITS
814-3324-01 | BOM | AR | HP CABINET RAISED FLOOR MOUNTING MATERIALS
814-3325-01 | BOM | AR | AC HP CABINET TO CONCRETE MOUNTING MATERIALS
NOTE 1: SEE FIGURES 1A-1L FOR EXTENSION BAR USAGE
FOR REFERENCE ONLY
FOR REFERENCE ONLY
FOR REFERENCE ONLY
FOR REFERENCE ONLY
FOR REFERENCE ONLY

## 870-3103-01 ITEM PICKLIST
TABLE A2: 870-3103-01 C-CLASS_AC_WRIGHT LINE CABINET WITH HARDWARE PART NUMBERS (FOR REF ONLY)
ORACLE P/N | MANUFACTURER'S PN | QTY | Oracle Bill of Materials shall be used. The part numbers shown below may not be the latest configuration and are shown for reference only. DESCRIPTION
CABINET HARDWARE 870-3103-01 (BOM includes cabinet label kit and assembly documentation. Cabinet and associated componments are separate orderable items)
870-3103-01 C-CLASS_AC_ WRIGHT LINE ASSY | BOM
| 658-0705-01 | 1 | ROHS_LABEL PART NO./REV. .25 X 1.50
| 658-0706-61 | 1 | LABEL SERIAL NO_ATYYWWMMXX
| 658-0770-11 | 1 | LABEL_CONSOLIDATED SYSTEM ID/REV_AC
| 658-0785-01 | 1 | 658 LABEL CAUTION ELECTROSTATIC SENSITIVE EQUIPMENT NTW
| 658-1066-01 | 1 | LABEL_WEEE_WASTE IN ELECTRICAL AND ELECTRONIC EQUIP_.40W X .50H_500 PER ROLL
| 804-0002-R | 1 | ROHS_ELASTIC WRIST STRAP ASSY STATIC CONTROL
| 616-0730-G01 | 5' | ROHS_ GROMMET_EDGE PROTECTOR_CONTINUOUS_PNL THK=.075 T0 .093 INCHES
| 617-0023-01 | 38 | LABEL_WHT BLANK_.65 X .20 POLYESTER FORM FEED_SELF ADHESIVE_THERMAL TX PART AND REV #
| 903-0122-01 | 1 | ROHS_LABEL BLANK_WHT_HIGH TEMP_0.250 H X 1.50 W H_DENS_THERMAL TRANSFER_ADH-BACK
| 821-0061-01 | 0 | TECHNICAL REFERENCE_AC_EAGLE XG_C-CLASS_WRIGHT LINE CABINET
| 892-0119-01 | 0 | SYSTEM INTERCONNECT_AC_EAGLE XG_C-CLASS_POWER_WRIGHT LINE CABINET
CABINET OPTIONS (BOM includes cabinet with associated hardware )(Pick One)
805-0585-01 WRIGHT LINE VZIAN008A84HSQH_AC READY CABINET_ SEISMIC_44U | BOM
| 804-1258-01 | 805-0585-01 BOM includes these items | CABINET_WRIGHT LINE_VZIAN008A84HSQH_SEISMIC_44U_SQ HOLES (NEED TO ORDER 50 AMP PDU MAX QTY 2)
| 804-3027-01 |  | PALLET WITH LONG RAMP_WRIGHT LINE
| 804-3031-01 |  | JANCHOR1_PARAMOUNT ANCHOR BRACKETS_WRIGHT LINE
| 804-1221-02 |  | DOOR_TOC_WRIGHT LINE_17500657_44U_24 INCHES WIDE
| 804-1655-01 |  | PANEL_BLANKING_19" EIA_1U_PACKAGE OF 10_ROHS
805-0583-01 WRIGHT LINE VZIAN008ASQH_ AC READY CABINET_ SEISMIC_40U | BOM
| 804-3028-01 | 805-0583-01 BOM includes these items | CABINET_WRIGHT LINE_40U_SQH (NEED TO ORDER 50 AMP PDU MAX QTY 2)
| 804-3027-01 |  | PALLET WITH LONG RAMP_WRIGHT LINE
| 804-3031-01 |  | JANCHOR1_PARAMOUNT ANCHOR BRACKETS_WRIGHT LINE
| 804-1221-01 |  | DOOR_TOC_WRIGHT LINE_17500655_40U_24 INCHES WIDE
| 804-1655-01 |  | PANEL_BLANKING_19" EIA_1U_PACKAGE OF 10_ROHS
POWER OPTIONS (VZW is not supplying their own PDU. This for REFERENCE ONLY)( PICK QTY 2 PER CABINET)
805-0584-01 WRIGHT LINE 17110314_ 50A PDU (THIS PDU HAS BEEN REPLACED BY THE 7095212 PDU KIT) | BOM
| 804-1254-01 | 1 | PDU_WRIGHT LINE 17110314_50A_AC_NA
| 804-0053-01 | 1 | POWER CORD_220V_10A_42" LONG_C-13 TO C-14_BLUE JACKET
| 804-0053-02 | 1 | POWER CORD_220V_10A_42" LONG_C-13 TO C-14_RED JACKET
| 804-1106-03 | 3 | POWER CORD_220V_15A_78" LONG_C-19 TO C-20_BLUE JACKET
| 804-1106-04 | 3 | POWER CORD_220V_15A_78" LONG_C-19 TO C-20_RED JACKET
7095212 VZIAN20150IPB, PDU WITH POWER CABLES, 50A, WRIGHT LINE | BOM
| 804-1254-01 | 1 | PDU_WRIGHT LINE VZIAN21650IPB_50A_AC_NA
| 804-0053-01 | 1 | POWER CORD_220V_10A_42" LONG_C-13 TO C-14_BLUE JACKET
| 804-0053-02 | 1 | POWER CORD_220V_10A_42" LONG_C-13 TO C-14_RED JACKET
| 804-1106-03 | 3 | POWER CORD_220V_15A_78" LONG_C-19 TO C-20_BLUE JACKET
| 804-1106-04 | 3 | POWER CORD_220V_15A_78" LONG_C-19 TO C-20_RED JACKET
NETWORK HARDWARE - The 4948E-F requires the panduit air duct. Order one for each switch. For Verizon switch will require one Red and one Blue Power Cable and a kit is released to support installation PN 7093416 One kit for each pair of switches this kit contains all power and data cables to mount 2 switches.
805-0592-02 | SEE BOM FOR PARTS LIST | AR | CISCO 4948E-F_AC_48 PORT ETHERNET SWITCH_002_ROHS 5/6
805-0593-01 | CDE2 | AR | PANDUIT CDE2_MODULAR SWITCH INLET DUCT_ROHS (FOR USE WITH 805-0592-02)
7093416 | SEE BOM FOR PARTS LIST | AR | ATO, SWITCH POWER CABLE KIT, WRIGHT LINE (FOR FACTORY INSTALLATION)
SFP MODULES FOR 4948 SERIES SWITCHES
805-0191-R01 | GLC-SX-MM= | AR | 1000BASE-SX_SFP FIBER OPTIC TRANSCEIVER_ROHS 5/6
805-0191-R02 | GLC-LH-SM= | AR | 1000BASE-LX/LH_SFP FIBER OPTIC TRANSCEIVER_ROHS 5/6
805-0191-R03 | SFP-10G-SR= | AR | 10G BASE-SR MULTIMODE SFP FIBER OPTIC TRANSCEIVER_ROHS 5/6
805-0191-R04 | SFP-10G-LR= | AR | 10G BASE-LR SINGLEMODE SFP FIBER OPTIC TRANSCEIVER_ROHS 5/6
DL380 GEN9 SERVERS for Verizon - Power cables are required and if the PDU kit is on the order then each PDU kit will provide one Red and one Blue Power Cable. If additional servers are required there is a kit released to support additional servers PN 7093412 One kit for each additional Server (SERVER C THRU SERVER K).
TR007457 | NA | AR | DL380 GEN9_AC_SERVER
c-7000 ENCLOSURE - OPTIONAL - PICK ONE, TWO OR THREE FOR AC CABINET (POWER CABLES ARE SUPPLIED WITH THE PDU KIT TO SUPPORT UP TO ONE ENCLOSURE, IF ADDITIONAL ENCLOSURES ARE REQUIRED USE CABLE KIT PN 709345.
805-0540-GXX | BOM | AR | C7000_AC_BLADE ENCLOSURE
805-0188-G01 | AH330A | AR | BRACE_SEISMIC_001_ROHS (ORDER ONE PER c7000 ENCLOSURE)
ENCLOSURE REAR BLADE SWITCH OPTIONS - OPTIONAL
805-0189-G01 | 516733-B21 | AR | 516733-B21_PROCURVE 6120XG_10 GBE_C7000 ENCLOSURE SWITCH_001_ROHS
805-0627-01 | 658247-B21 | AR | HP 658247-B21_BLADE SWITCH_C-CLASS_HP6125G_1GB_ROHS
805-0190-G01 | 406740-B21 | AR | HP-406740-B21_1GBE_PASS THRU MODULE_001_ROHS
7093049 | 711307-B21 | AR | ATO, BLADE SWITCH, 10GBE, HP 6125XLG (FOR FACTORY INSTALLATION)
ORACLE SERVER - SFP MODULE OPTIONS
X2129A-N | AFBR-709DMZ-SN1 | AR | SCVR, 850NM, 1/10GBPS DUAL RA
5562A-Z | AFCT-701SDDZ-SN1 |  | 10GbE/1GbE SRP+ TRANSCEIVER, LR
SFP MODULES FOR 804-2185-R01 CISCO 3020 SWITCH
805-0595-G01 | 378929-B21 | AR | HP 378929-B21_1000BASE-SX_MULTIMODE SFP FIBER OPTIC TRANSCEIVER_ROHS
SFP MODULES FOR 805-0189-G01 PROCURVE 6120XG SWITCH
805-0567-G01 | 453154-B21 | AR | 453154-B21_1000BASE-T_SFP COPPER TRANSCEIVER_ROHS
805-0567-G02 | 453151-B21 | AR | 453151-B21_1000BASE-SX_MULTIMODE SFP FIBER OPTIC TRANSCEIVER_ROHS
805-0567-G03 | 455883-B21 | AR | 455883-B21_10GBASE-SR_MULTIMODE SFP FIBER OPTIC TRANSCEIVER_ROHS
805-0567-G04 | 455886-B21 | AR | 455886-B21_10GBASE-LR_SINGLEMODE SFP FIBER OPTIC TRANSCEIVER_ROHS
SFP MODULES FOR 805-0627-01 HP 6125G SWITCH
805-0628-01 | JD089B | AR | JD089B_HP_X120_SFP RJ45 T TRANSCEIVER_ROHS 5/6
SFP MODULES FOR 7093053 HP 6125XLG SWITCH
805-0628-01 | JD089B | AR | JD089B_HP_X120_SFP RJ45 T TRANSCEIVER_ROHS 5/6
7093055 | JD092B | AR | JD092B_SFP+ TRANSCEIVER, 10GBE, HP X130 LC SR 850NM
HALF HEIGHT BLADE OPTIONS - OPTIONAL
TR007457 | NA | AR | GEN SPEC_BL460C GEN9_BLADE SERVER
STORAGE BLADE OPTIONS
805-0619-04 | SEE ORACLE BOM | 1 | HP_STORAGE BLADE QW918A_600GB HARD DRIVES_ROHS
805-0619-03 | SEE ORACLE BOM | 1 | HP_STORAGE BLADE QW918A_146GB HARD DRIVES_ROHS
805-0619-02 | SEE ORACLE BOM | 1 | HP AP882A_STORAGE BLADE_600GB HARD DRIVES_ROHS
805-0619-01 | SEE ORACLE BOM | 1 | HP_STORAGE BLADE_146GB HARD DRIVES_ROHS
ASSEMBLY MATERIAL INSTALLATION KITS (FOR FACTORY INSTALLATION) -
658-1158-01 thru 658-1158-07 | TEK SPEC | AR | LABEL_FRAME ID_EXG-00, EXG-01, EXG-02, EXG-03, EXG-04, EXG-05, EXG-06
7093412 | SEE ORACLE BOM | AR | ATO, SERVER POWER CABLE KIT, WRIGHT LINE (FOR FACTORY INSTALLATION)
7093416 | SEE ORACLE BOM | AR | ATO, SWITCH POWER CABLE KIT, WRIGHT LINE (FOR FACTORY INSTALLATION)
WRIGHT LINE SPECIFIC FLOOR MOUNTING KITS
804-3031-01 | WRIGHT LINE JANCHOR1 | AR | JANCHOR1_PARAMOUNT ANCHOR BRACKETS_WRIGHT LINE
804-3029-01 | WRIGHT LINE PMKITEL | AR | PMKITEL_ELECTRICAL ISOLATION KIT_WRIGHT LINE
804-3030-01 | WRIGHT LINE PMKITFL | AR | PMKITFL_FLOOR ISOLATION KIT_WRIGHT LINE
MISC SUPPORTING WRIGHT LINE HARDWARE
804-1221-01 | WRIGHT LINE 17500655 | AR | DOOR_TOC_WRIGHT LINE_17500655_40U_24 INCHES WIDE (NOT SUPPORTED ANY LONGER)
804-1221-02 | WRIGHT LINE 17500657 | AR | DOOR_TOC_WRIGHT LINE_17500657_44U_24 INCHES WIDE (NOT SUPPORTED ANY LONGER)
804-3027-01 | WRIGHT LINE 999991 | AR | PALLET WITH LONG RAMP_WRIGHT LINE
804-1656-01 | WRIGHT LINE JHBLKCG1032 | AR | WRIGHT LINE JHBLKCG1032_10-32 CAGE NUT AND 10-32 X .625 LONG BLACK SCREW_KIT_QTY 500_ROHS
805-0594-01 | WRIGHT LINE JSPS7740 | AR | WRIGHT LINE SIDE PANEL_40UX40"D SOLID_INCLUDES TOP CAP_ROHS
805-0594-02 | WRIGHT LINE JSPS8440 | AR | WRIGHT LINE SIDE PANEL_44UX40"D SOLID_INCLUDES TOP CAP_ROHS
804-0053-01 | WRIGHT LINE PC2208IIB | AR | POWER CORD_220V_10A_42" LONG_C-13 TO C-14_BLUE JACKET
804-0053-02 | WRIGHT LINE PC2208IIR | AR | POWER CORD_220V_10A_42" LONG_C-13 TO C-14_RED JACKET
804-0053-03 | WRIGHT LINE PC2206IIB | AR | POWER CORD_220V_10A_78" LONG_C-13 TO C-14_BLUE JACKET
804-0053-04 | WRIGHT LINE PC2206IIR | AR | POWER CORD_220V_10A_78" LONG_C-13 TO C-14_RED JACKET
804-1106-01 | WRIGHT LINE PC2210IIB | AR | POWER CORD_220V_16A_42" LONG_C-19 TO C-20_BLUE JACKET
804-1106-02 | WRIGHT LINE PC2210IIR | AR | POWER CORD_220V_16A_42" LONG_C-19 TO C-20_RED JACKET
804-1106-03 | WRIGHT LINE PC2207IIB | AR | POWER CORD_220V_15A_78" LONG_C-19 TO C-20_BLUE JACKET
804-1106-04 | WRIGHT LINE PC2207IIR | AR | POWER CORD_220V_15A_78" LONG_C-19 TO C-20_RED JACKET
804-1259-01 | WRIGHT LINE 17500970 | AR | TOC SEALING KIT_WRIGHT LINE_17500970_24 INCHES WIDE_BRUSH
804-1655-01 | WRIGHT LINE V319F01U10BLK | AR | PANEL_BLANKING_19" EIA_1U_PACKAGE OF 10_ROHS
7300465 | ORACLE SPEC | AR | LABEL SHEET, FRAME AND COMPONENT IDENTIFICATION
7093415 | SEE BOM FOR PARTS LIST | AR | TLA, ENCLOSURE POWER CABLE KIT, WRIGHT LINE
7093414 | SEE BOM FOR PARTS LIST | AR | TLA, SERVER POWER CABLE KIT, WRIGHT LINE
7093417 | SEE BOM FOR PARTS LIST | AR | TLA, SWITCH POWER CABLE KIT, WRIGHT LINE
7093054 | SEE BOM FOR PARTS LIST | AR | TLA, BLADE SWITCH, 10GBE, HP 6125XLG
7093057 | SEE BOM FOR PARTS LIST | AR | TLA, SFP+ TRANSCEIVER, 10GBE, LC SR 850NM, HP X130
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
870-3103-01 ITEM PICKLIST TAB
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY
FOR
REFERENCE
ONLY

## SINGLE PHASE GEN9 CAB LAY
SINGLE PHASE AC LAYOUT TAB
|  | U | FIGURE 1A: SINGLE PHASE 870-3111-01 CABINET WITH Cisco 4948E-F, (3) Encl, (GEN9 1x2U SERVER/ 2 DL360 GEN9) NOTE 1 BELOW | [10 empty] | U | FIGURE 1B: SINGLE PHASE 870-3111-01 CABINET WITH Cisco 4948E-F, (2) Encl, (GEN9 6x2U SERVERS/ 12 DL360 GEN9) NOTE 1 BELOW | [11 empty] | U | FIGURE 1C: SINGLE PHASE 870-3111-01 CABINET WITH Cisco 4948E-F, (1) Encl, (GEN9 11x2U SERVERS/ 12 DL360 GEN9) NOTE 1 BELOW
|  | 42 | [11 empty] | 42 | [12 empty] | 42
|  | 41 | [11 empty] | 41 | [12 empty] | 41
|  | 40 | OPEN - FILLER PANEL | [10 empty] | 40 | [12 empty] | 40
|  | 39 | OPEN - FILLER PANEL | [10 empty] | 39 | [12 empty] | 39
|  | 38 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9 | [6 empty] | 38 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9 | [7 empty] | 38 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9
|  | 37 |  |  |  |  | SERVER B DL360 GEN9 | [6 empty] | 37 |  |  |  |  | SERVER B DL360 GEN9 | [7 empty] | 37 |  |  |  |  | SERVER B DL360 GEN9
|  | 36 | (cxen3-bay1) BLADE | (cxen3-bay2) BLADE | (cxen3-bay3) BLADE | (cxen3-bay4) BLADE | (cxen3-bay4) BLADE | (cxen3-bay4) BLADE | (cxen3-bay7) BLADE | (cxen3-bay8) BLADE |  |  |  | 36 | SERVER B DL380 GEN9 |  |  |  | SERVER C DL360 GEN9 | [7 empty] | 36 | SERVER B DL380 GEN9 |  |  |  | SERVER C DL360 GEN9
|  | 35 | [11 empty] | 35 |  |  |  |  | SERVER D DL360 GEN9 | [7 empty] | 35 |  |  |  |  | SERVER D DL360 GEN9
|  | 34 | [11 empty] | 34 | SERVER C DL380 GEN9 |  |  |  | SERVER E DL360 GEN9 | [7 empty] | 34 | SERVER C DL380 GEN9 |  |  |  | SERVER E DL360 GEN9
|  | 33 | [11 empty] | 33 |  |  |  |  | SERVER F DL360 GEN9 | [7 empty] | 33 |  |  |  |  | SERVER F DL360 GEN9
|  | 32 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  | 32 | SERVER D DL380 GEN9 |  |  |  | SERVER G DL360 GEN9 | [7 empty] | 32 | SERVER D DL380 GEN9 |  |  |  | SERVER G DL360 GEN9
|  | 31 | (cxen3-bay9) BLADE | (cxen3-bay10) BLADE | (cxen3-bay11) BLADE | (cxen3-bay12) BLADE | (cxen3-bay13) BLADE | (cxen3-bay14) BLADE | (cxen3-bay15) BLADE | (cxen3-bay16) BLADE |  |  |  | 31 |  |  |  |  | SERVER H DL360 GEN9 | [7 empty] | 31 |  |  |  |  | SERVER H DL360 GEN9
|  | 33 32: 30 |  |  |  | 30 | SERVER E DL380 GEN9 |  |  |  | SERVER I DL360 GEN9 | [7 empty] | 30 | SERVER E DL380 GEN9 |  |  |  | SERVER I DL360 GEN9
|  | 33 32: 29 |  |  |  | 29 |  |  |  |  | SERVER J DL360 GEN9 | [7 empty] | 29 |  |  |  |  | SERVER J DL360 GEN9
| A1-4 EXT. BAR | 33 32: 28 | B1-4 EXT. BAR |  | A1-4 EXT. BAR | 28 | SERVER F DL380 GEN9 |  |  |  | SERVER K DL360 GEN9 |  |  |  | B1-4 EXT. BAR |  |  | A1-4 EXT. BAR | 28 | SERVER F DL380 GEN9 |  |  |  | SERVER K DL360 GEN9 |  |  |  | B1-4 EXT. BAR
|  | 27 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  | 27 |  |  |  |  | SERVER L DL360 GEN9 | [7 empty] | 27 |  |  |  |  | SERVER L DL360 GEN9
|  | 26 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE |  |  |  | 26 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE |  |  |  |  | 26 | SERVER G DL380 GEN9 |  |  |  | FILLER PANEL
|  | 28 27: 25 |  |  |  | 25 | [12 empty] | 25 |  |  |  |  | FILLER PANEL
|  | 28 27: 24 |  |  |  | 24 | [12 empty] | 24 | SERVER H DL380 GEN9 |  |  |  | FILLER PANEL
|  | 28 27: 23 |  |  |  | 23 | [12 empty] | 23 |  |  |  |  | FILLER PANEL
| A3-4 EXT. BAR | 22 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | B3-4 EXT. BAR | A3-3 EXT. BAR | A3-4 EXT. BAR | 22 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | B3-4 EXT. BAR | B3-3 EXT. BAR | A3-3 EXT. BAR | A3-4 EXT. BAR | 22 | SERVER I DL380 GEN9 |  |  |  | FILLER PANEL |  |  |  | B3-4 EXT. BAR | B3-3 EXT. BAR
|  | 21 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE |  |  |  | 21 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE |  |  |  |  | 21 |  |  |  |  | FILLER PANEL
|  | 23 22: 20 |  |  |  | 20 | [12 empty] | 20 | SERVER J DL380 GEN9 |  |  |  | FILLER PANEL
|  | 23 22: 19 |  |  |  | 19 | [12 empty] | 19 |  |  |  |  | FILLER PANEL
|  | 23 22: 18 |  |  |  | 18 | [12 empty] | 18 | SERVER K DL380 GEN9 |  |  |  | FILLER PANEL
|  | 17 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  | 17 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 17 |  |  |  |  | FILLER PANEL
|  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 18 17: 15 |  |  |  | 15 | [12 empty] | 15
|  | 18 17: 14 |  |  |  | 14 | [12 empty] | 14
|  | 18 17: 13 |  |  |  | 13 | [12 empty] | 13
|  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 13 12: 10 |  |  |  | 10 | [12 empty] | 10
|  | 13 12: 9 |  |  |  | 9 | [12 empty] | 9
|  | 13 12: 8 |  |  |  | 8 | [12 empty] | 8
|  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 8 7: 6; 8 9: PDU B3 |  |  |  | 6 | PDU B3 | [11 empty] | 6 | PDU B3
|  | 8 7: 5; 8 9: PDU A3 |  |  |  | 5 | PDU A3 | [11 empty] | 5 | PDU A3
|  | 8 7: 4; 8 9: PDU B2 |  |  |  | 4 | PDU B2 | [8 empty] | HP PN BW929A (Filler Panel Pack of 100) (REF) |  |  | 4 | FILLER PANEL
|  | 8 7: 3; 8 9: PDU A2 |  |  |  | 3 | PDU A2 | [11 empty] | 3 | FILLER PANEL
|  | 8 7: 2; 8 9: PDU B1 |  |  |  | 2 | PDU B1 | [11 empty] | 2 | PDU B1
|  | 8 7: 1; 8 9: PDU A1 |  |  |  | 1 | PDU A1 | [11 empty] | 1 | PDU A1
NOTE 1: ALL SERVERS ARE FRONT MOUNTED AND THE 4948E-F SWITCHES WILL BE REAR MOUNTED. PDUS ARE FRONT MOUNTED. INSTALL THE PANDUIT AIR DUCT FOR SWITCH "A" IN U39-U40 AND THE AIR DUCT FOR SWITCH B IN U41-U42. AIR DUCT IS 2U HIGH AND THE AIR INTAKE GRILL SHOULD BE MOUNTED IN THE FRONT OF THE CABINET. THE SWITCHES WILL MOUNT IN THE AIR DUCT WITH THE ETHERNET PORTS FACING THE REAR OF THE CABINET, SEE PANDUIT ASSEMBLY INSTRUCTIONS AND FIGURE 2 AND 3. THE CABLE MANAGEMENT BARS ARE INCLUDED IN THE SWITCH ASSEMBLY MATERIALS KIT. MOUNT THE CABLE MANAGEMENT BARS TO THE REAR OF THE CABINET TO THE AIR DUCT MOUNTING BRACKET SEE FIGURE 3. FILLER PANELS IN ALL OPEN U LOCATIONS (SEE ASSEMBLY NOTES 6,7,8,9,10,11 AND 17).
SWITCH A
SWITCH A
SWITCH A
SWITCH B
SWITCH B
SWITCH B

## THREE PHASE GEN9 CAB LAY
THREE PHASE AC LAYOUT TAB
|  | U | FIGURE 1D: THREE PHASE 870-3111-01 CABINET WITH Cisco 4948E-F, (3) Encl, (GEN9 1x2U SERVER/ 2 DL360 GEN9) NOTE 1 BELOW | [11 empty] | U | FIGURE 1E: THREE PHASE 870-3111-01 CABINET WITH Cisco 4948E-F, (2) Encl, (GEN9 6x2U SERVERS/ 12 DL360 GEN9) NOTE 1 BELOW | [11 empty] | U | FIGURE 1F: THREE PHASE 870-3111-01 CABINET WITH Cisco 4948E-F, (1) Encl, (GEN9 11x2U SERVERS/ 12 DL360 GEN9) NOTE 1 BELOW
|  | 42 | [12 empty] | 42 | [12 empty] | 42
|  | 41 | [12 empty] | 41 | [12 empty] | 41
|  | 40 | OPEN - FILLER PANEL | [11 empty] | 40 | [12 empty] | 40
|  | 39 | OPEN - FILLER PANEL | [11 empty] | 39 | [12 empty] | 39
|  | 38 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9 | [7 empty] | 38 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9 | [7 empty] | 38 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9
|  | 37 |  |  |  |  | SERVER B DL360 GEN9 | [7 empty] | 37 |  |  |  |  | SERVER B DL360 GEN9 | [7 empty] | 37 |  |  |  |  | SERVER B DL360 GEN9
|  | 36 | (cxen3-bay1) BLADE | (cxen3-bay2) BLADE | (cxen3-bay3) BLADE | (cxen3-bay4) BLADE | (cxen3-bay4) BLADE | (cxen3-bay4) BLADE | (cxen3-bay7) BLADE | (cxen3-bay8) BLADE |  |  |  |  | 36 | SERVER B DL380 GEN9 |  |  |  | SERVER C DL360 GEN9 | [7 empty] | 36 | SERVER B DL380 GEN9 |  |  |  | SERVER C DL360 GEN9
|  | 35 | [12 empty] | 35 |  |  |  |  | SERVER D DL360 GEN9 | [7 empty] | 35 |  |  |  |  | SERVER D DL360 GEN9
|  | 34 | [12 empty] | 34 | SERVER C DL380 GEN9 |  |  |  | SERVER E DL360 GEN9 | [7 empty] | 34 | SERVER C DL380 GEN9 |  |  |  | SERVER E DL360 GEN9
|  | 33 | [12 empty] | 33 |  |  |  |  | SERVER F DL360 GEN9 | [7 empty] | 33 |  |  |  |  | SERVER F DL360 GEN9
|  | 32 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 32 | SERVER D DL380 GEN9 |  |  |  | SERVER G DL360 GEN9 | [7 empty] | 32 | SERVER D DL380 GEN9 |  |  |  | SERVER G DL360 GEN9
|  | 31 | (cxen3-bay9) BLADE | (cxen3-bay10) BLADE | (cxen3-bay11) BLADE | (cxen3-bay12) BLADE | (cxen3-bay13) BLADE | (cxen3-bay14) BLADE | (cxen3-bay15) BLADE | (cxen3-bay16) BLADE |  |  |  |  | 31 |  |  |  |  | SERVER H DL360 GEN9 | [7 empty] | 31 |  |  |  |  | SERVER H DL360 GEN9
|  | 33 32: 30 |  |  |  |  | 30 | SERVER E DL380 GEN9 |  |  |  | SERVER I DL360 GEN9 | [7 empty] | 30 | SERVER E DL380 GEN9 |  |  |  | SERVER I DL360 GEN9
|  | 33 32: 29 |  |  |  |  | 29 |  |  |  |  | SERVER J DL360 GEN9 | [7 empty] | 29 |  |  |  |  | SERVER J DL360 GEN9
A1-5 EXT. BAR | A1-6 EXT. BAR | 33 32: 28 | B1-6 EXT. BAR | B1-5 EXT. BAR | A1-5 EXT. BAR | A1-6 EXT. BAR | 28 | SERVER F DL380 GEN9 |  |  |  | SERVER K DL360 GEN9 |  |  |  | B1-6 EXT. BAR | B1-5 EXT. BAR | A1-5 EXT. BAR | A1-6 EXT. BAR | 28 | SERVER F DL380 GEN9 |  |  |  | SERVER K DL360 GEN9 |  |  |  | B1-6 EXT. BAR | B1-5 EXT. BAR
|  | 27 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 27 |  |  |  |  | SERVER L DL360 GEN9 | [7 empty] | 27 |  |  |  |  | SERVER L DL360 GEN9
|  | 26 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE |  |  |  |  | 26 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE |  |  |  |  | 26 | SERVER G DL380 GEN9 |  |  |  | FILLER PANEL
|  | 28 27: 25 |  |  |  |  | 25 | [12 empty] | 25 |  |  |  |  | FILLER PANEL
|  | 28 27: 24 |  |  |  |  | 24 | [12 empty] | 24 | SERVER H DL380 GEN9 |  |  |  | FILLER PANEL
|  | 28 27: 23 |  |  |  |  | 23 | [12 empty] | 23 |  |  |  |  | FILLER PANEL
|  | 22 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  | A1-4 EXT. BAR | 22 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | B1-4 EXT. BAR |  |  | A1-4 EXT. BAR | 22 | SERVER I DL380 GEN9 |  |  |  | FILLER PANEL |  |  |  | B1-4 EXT. BAR
|  | 21 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE |  |  |  |  | 21 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE |  |  |  |  | 21 |  |  |  |  | FILLER PANEL
|  | 23 22: 20 |  |  |  |  | 20 | [12 empty] | 20 | SERVER J DL380 GEN9 |  |  |  | FILLER PANEL
|  | 23 22: 19 |  |  |  |  | 19 | [12 empty] | 19 |  |  |  |  | FILLER PANEL
|  | 23 22: 18 |  |  |  |  | 18 | [12 empty] | 18 | SERVER K DL380 GEN9 |  |  |  | FILLER PANEL
|  | 17 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 17 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 17 |  |  |  |  | FILLER PANEL
|  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 18 17: 15 |  |  |  |  | 15 | [12 empty] | 15
|  | 18 17: 14 |  |  |  |  | 14 | [12 empty] | 14
|  | 18 17: 13 |  |  |  |  | 13 | [12 empty] | 13
|  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 13 12: 10 |  |  |  |  | 10 | [12 empty] | 10
|  | 13 12: 9 |  |  |  |  | 9 | [12 empty] | 9
|  | 13 12: 8 |  |  |  |  | 8 | [12 empty] | 8
|  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 8 7: 6; 8 9: FILLER PANEL |  |  |  |  | 6 | FILLER PANEL | [8 empty] | HP PN BW929A (Filler Panel Pack of 100) (REF) |  |  | 6 | FILLER PANEL
|  | 8 7: 5; 8 9: FILLER PANEL |  |  |  |  | 5 | FILLER PANEL | [11 empty] | 5 | FILLER PANEL
|  | 8 7: 4; 8 9: PDU B2 |  |  |  |  | 4 | PDU B2 | [11 empty] | 4 | FILLER PANEL
|  | 8 7: 3; 8 9: PDU A2 |  |  |  |  | 3 | PDU A2 | [11 empty] | 3 | FILLER PANEL
|  | 8 7: 2; 8 9: PDU B1 |  |  |  |  | 2 | PDU B1 | [11 empty] | 2 | PDU B1
|  | 8 7: 1; 8 9: PDU A1 |  |  |  |  | 1 | PDU A1 | [11 empty] | 1 | PDU A1
NOTE 1: ALL SERVERS ARE FRONT MOUNTED AND THE 4948E-F SWITCHES WILL BE REAR MOUNTED. PDUS ARE FRONT MOUNTED. INSTALL THE PANDUIT AIR DUCT FOR SWITCH "A" IN U39-U40 AND THE AIR DUCT FOR SWITCH B IN U41-U42. AIR DUCT IS 2U HIGH AND THE AIR INTAKE GRILL SHOULD BE MOUNTED IN THE FRONT OF THE CABINET. THE SWITCHES WILL MOUNT IN THE AIR DUCT WITH THE ETHERNET PORTS FACING THE REAR OF THE CABINET, SEE PANDUIT ASSEMBLY INSTRUCTIONS AND FIGURE 2 AND 3. THE CABLE MANAGEMENT BARS ARE INCLUDED IN THE 814-0033-02 ASSEMBLY MATERIALS KIT. MOUNT THE CABLE MANAGEMENT BARS TO THE REAR OF THE CABINET TO THE AIR DUCT MOUNTING BRACKET SEE FIGURE 3. FILLER PANELS IN ALL OPEN U LOCATIONS (SEE ASSEMBLY NOTES 6,7,8,9,10,11 AND 17).
SWITCH A
SWITCH A
SWITCH A
SWITCH B
SWITCH B
SWITCH B

## SINGLE PHASE GEN8_GEN9 CAB LAY
SINGLE PHASE AC LAYOUT TAB
|  | U | FIGURE 1G: Comingled GEN8 and GEN9 Server with Single Phase Pwr and Cisco 4948E-F, (3) Encl, (1x2U SERVER/ 2 DL360) NOTE 1 BELOW | [10 empty] | U | FIGURE 1H: Comingled GEN8 and GEN9 Server with Single Phase Pwr and Cisco 4948E-F, (2) Encl, (6x2U SERVERS/ 12 DL360) NOTE 1 BELOW | [11 empty] | U | FIGURE 1I: Comingled GEN8 and GEN9 Server with Single Phase Pwr and Cisco 4948E-F, (1) Encl, (11x2U SERVERS/ 12 DL360) NOTE 1 BELOW
|  | 42 | [11 empty] | 42 | [12 empty] | 42
|  | 41 | [11 empty] | 41 | [12 empty] | 41
|  | 40 | OPEN - FILLER PANEL | [10 empty] | 40 | [12 empty] | 40
|  | 39 | OPEN - FILLER PANEL | [10 empty] | 39 | [12 empty] | 39
|  | 38 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9) | [6 empty] | 38 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9) | [7 empty] | 38 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9)
|  | 37 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9) | [6 empty] | 37 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9) | [7 empty] | 37 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9)
|  | 36 | (cxen3-bay1) BLADE | (cxen3-bay2) BLADE | (cxen3-bay3) BLADE | (cxen3-bay4) BLADE | (cxen3-bay4) BLADE | (cxen3-bay4) BLADE | (cxen3-bay7) BLADE | (cxen3-bay8) BLADE |  |  |  | 36 | SERVER B DL380 (GEN8 OR GEN9) |  |  |  | SERVER C DL360 (GEN8 OR GEN9) | [7 empty] | 36 | SERVER B DL380 (GEN8 OR GEN9) |  |  |  | SERVER C DL360 (GEN8 OR GEN9)
|  | 35 | [11 empty] | 35 |  |  |  |  | SERVER D DL360 (GEN8 OR GEN9) | [7 empty] | 35 |  |  |  |  | SERVER D DL360 (GEN8 OR GEN9)
|  | 34 | [11 empty] | 34 | SERVER C DL380 (GEN8 OR GEN9) |  |  |  | SERVER E DL360 (GEN8 OR GEN9) | [7 empty] | 34 | SERVER C DL380 (GEN8 OR GEN9) |  |  |  | SERVER E DL360 (GEN8 OR GEN9)
|  | 33 | [11 empty] | 33 |  |  |  |  | SERVER F DL360 (GEN8 OR GEN9) | [7 empty] | 33 |  |  |  |  | SERVER F DL360 (GEN8 OR GEN9)
|  | 32 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  | 32 | SERVER D DL380 (GEN8 OR GEN9) |  |  |  | SERVER G DL360 (GEN8 OR GEN9) | [7 empty] | 32 | SERVER D DL380 (GEN8 OR GEN9) |  |  |  | SERVER G DL360 (GEN8 OR GEN9)
|  | 31 | (cxen3-bay9) BLADE | (cxen3-bay10) BLADE | (cxen3-bay11) BLADE | (cxen3-bay12) BLADE | (cxen3-bay13) BLADE | (cxen3-bay14) BLADE | (cxen3-bay15) BLADE | (cxen3-bay16) BLADE |  |  |  | 31 |  |  |  |  | SERVER H DL360 (GEN8 OR GEN9) | [7 empty] | 31 |  |  |  |  | SERVER H DL360 (GEN8 OR GEN9)
|  | 33 32: 30 |  |  |  | 30 | SERVER E DL380 (GEN8 OR GEN9) |  |  |  | SERVER I DL360 (GEN8 OR GEN9) | [7 empty] | 30 | SERVER E DL380 (GEN8 OR GEN9) |  |  |  | SERVER I DL360 (GEN8 OR GEN9)
|  | 33 32: 29 |  |  |  | 29 |  |  |  |  | SERVER J DL360 (GEN8 OR GEN9) | [7 empty] | 29 |  |  |  |  | SERVER J DL360 (GEN8 OR GEN9)
| A1-4 EXT. BAR | 33 32: 28 | B1-4 EXT. BAR |  | A1-4 EXT. BAR | 28 | SERVER F DL380 (GEN8 OR GEN9) |  |  |  | SERVER K DL360 (GEN8 OR GEN9) |  |  |  | B1-4 EXT. BAR |  |  | A1-4 EXT. BAR | 28 | SERVER F DL380 (GEN8 OR GEN9) |  |  |  | SERVER K DL360 (GEN8 OR GEN9) |  |  |  | B1-4 EXT. BAR
|  | 27 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  | 27 |  |  |  |  | SERVER L DL360 (GEN8 OR GEN9) | [7 empty] | 27 |  |  |  |  | SERVER L DL360 (GEN8 OR GEN9)
|  | 26 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE |  |  |  | 26 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE |  |  |  |  | 26 | SERVER G DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 28 27: 25 |  |  |  | 25 | [12 empty] | 25 |  |  |  |  | FILLER PANEL
|  | 28 27: 24 |  |  |  | 24 | [12 empty] | 24 | SERVER H DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 28 27: 23 |  |  |  | 23 | [12 empty] | 23 |  |  |  |  | FILLER PANEL
| A3-4 EXT. BAR | 22 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | B3-4 EXT. BAR | A3-3 EXT. BAR | A3-4 EXT. BAR | 22 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | B3-4 EXT. BAR | B3-3 EXT. BAR | A3-3 EXT. BAR | A3-4 EXT. BAR | 22 | SERVER I DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL |  |  |  | B3-4 EXT. BAR | B3-3 EXT. BAR
|  | 21 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE |  |  |  | 21 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE |  |  |  |  | 21 |  |  |  |  | FILLER PANEL
|  | 23 22: 20 |  |  |  | 20 | [12 empty] | 20 | SERVER J DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 23 22: 19 |  |  |  | 19 | [12 empty] | 19 |  |  |  |  | FILLER PANEL
|  | 23 22: 18 |  |  |  | 18 | [12 empty] | 18 | SERVER K DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 17 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  | 17 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 17 |  |  |  |  | FILLER PANEL
|  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 18 17: 15 |  |  |  | 15 | [12 empty] | 15
|  | 18 17: 14 |  |  |  | 14 | [12 empty] | 14
|  | 18 17: 13 |  |  |  | 13 | [12 empty] | 13
|  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 13 12: 10 |  |  |  | 10 | [12 empty] | 10
|  | 13 12: 9 |  |  |  | 9 | [12 empty] | 9
|  | 13 12: 8 |  |  |  | 8 | [12 empty] | 8
|  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 8 7: 6; 8 9: PDU B3 |  |  |  | 6 | PDU B3 | [11 empty] | 6 | PDU B3
|  | 8 7: 5; 8 9: PDU A3 |  |  |  | 5 | PDU A3 | [8 empty] | HP PN BW929A (Filler Panel Pack of 100) (REF) |  |  | 5 | PDU A3
|  | 8 7: 4; 8 9: PDU B2 |  |  |  | 4 | PDU B2 | [11 empty] | 4 | FILLER PANEL
|  | 8 7: 3; 8 9: PDU A2 |  |  |  | 3 | PDU A2 | [11 empty] | 3 | FILLER PANEL
|  | 8 7: 2; 8 9: PDU B1 |  |  |  | 2 | PDU B1 | [11 empty] | 2 | PDU B1
|  | 8 7: 1; 8 9: PDU A1 |  |  |  | 1 | PDU A1 | [11 empty] | 1 | PDU A1
NOTE 1: THE GEN8 AND GEN9 SERVERS CAN BE MIXED IN THE SAME CABINET. THE SERVERS SHOWN ABOVE IN FIGURE 1D, 1E AND 1F COULD BE DL380 GEN8 SERVER OR THE HP DL380 GEN9 SERVER. BOTH SERVERS ARE 2U SERVER SO THERE IS NOT RESTRICTIONS FOR INSTALLING A HP DL380 GEN9 SERVER IN ANY AVAILABLE SERVER POSITION.THE GEN8 AND GEN9 SERVERS CAN BE MIXED IN THE SAME CABINET. ALL SERVERS ARE FRONT MOUNTED AND THE 4948E-F SWITCHES WILL BE REAR MOUNTED. PDUS ARE FRONT MOUNTED. INSTALL THE PANDUIT AIR DUCT FOR SWITCH "A" IN U39-U40 AND THE AIR DUCT FOR SWITCH B IN U41-U42. AIR DUCT IS 2U HIGH AND THE AIR INTAKE GRILL SHOULD BE MOUNTED IN THE FRONT OF THE CABINET. THE SWITCHES WILL MOUNT IN THE AIR DUCT WITH THE ETHERNET PORTS FACING THE REAR OF THE CABINET, SEE PANDUIT ASSEMBLY INSTRUCTIONS AND FIGURE 2 AND 3. THE CABLE MANAGEMENT BARS ARE INCLUDED IN THE 814-0033-02 ASSEMBLY MATERIALS KIT. MOUNT THE CABLE MANAGEMENT BARS TO THE REAR OF THE CABINET TO THE AIR DUCT MOUNTING BRACKET SEE FIGURE 3. THE 2U SERVERS CAN BE EITHER HP DL380 OR NETRA X3-2 (SEE PICK LIST FOR DETAILS). FILLER PANELS IN ALL OPEN U LOCATIONS (SEE ASSEMBLY NOTES 6,7,8,9,10,11 AND 17).
SWITCH A
SWITCH A
SWITCH A
SWITCH B
SWITCH B
SWITCH B

## THREE PHASE GEN8_GEN9 CAB LAY
THREE PHASE AC LAYOUT TAB
|  | U | FIGURE 1J: Comingled GEN8 and GEN9 Server with Three Phase Power and Cisco 4948E-F, (3) Encl, (1x2U SERVER/ 2 DL360) NOTE 1 BELOW | [11 empty] | U | FIGURE 1K: Comingled GEN8 and GEN9 Server with Three Phase Power and Cisco 4948E-F, (2) Encl, (6x2U SERVERS/ 12 DL360) NOTE 1 BELOW | [11 empty] | U | FIGURE 1L: Comingled GEN8 and GEN9 Server with Three Phase Power and Cisco 4948E-F, (1) Encl, (11x2U SERVERS/ 12 DL360) NOTE 1 BELOW
|  | 42 | [12 empty] | 42 | [12 empty] | 42
|  | 41 | [12 empty] | 41 | [12 empty] | 41
|  | 40 | OPEN - FILLER PANEL | [11 empty] | 40 | [12 empty] | 40
|  | 39 | OPEN - FILLER PANEL | [11 empty] | 39 | [12 empty] | 39
|  | 38 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9) | [7 empty] | 38 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9) | [7 empty] | 38 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9)
|  | 37 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9) | [7 empty] | 37 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9) | [7 empty] | 37 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9)
|  | 36 | (cxen3-bay1) BLADE | (cxen3-bay2) BLADE | (cxen3-bay3) BLADE | (cxen3-bay4) BLADE | (cxen3-bay4) BLADE | (cxen3-bay4) BLADE | (cxen3-bay7) BLADE | (cxen3-bay8) BLADE |  |  |  |  | 36 | SERVER B DL380 (GEN8 OR GEN9) |  |  |  | SERVER C DL360 (GEN8 OR GEN9) | [7 empty] | 36 | SERVER B DL380 (GEN8 OR GEN9) |  |  |  | SERVER C DL360 (GEN8 OR GEN9)
|  | 35 | [12 empty] | 35 |  |  |  |  | SERVER D DL360 (GEN8 OR GEN9) | [7 empty] | 35 |  |  |  |  | SERVER D DL360 (GEN8 OR GEN9)
|  | 34 | [12 empty] | 34 | SERVER C DL380 (GEN8 OR GEN9) |  |  |  | SERVER E DL360 (GEN8 OR GEN9) | [7 empty] | 34 | SERVER C DL380 (GEN8 OR GEN9) |  |  |  | SERVER E DL360 (GEN8 OR GEN9)
|  | 33 | [12 empty] | 33 |  |  |  |  | SERVER F DL360 (GEN8 OR GEN9) | [7 empty] | 33 |  |  |  |  | SERVER F DL360 (GEN8 OR GEN9)
|  | 32 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 32 | SERVER D DL380 (GEN8 OR GEN9) |  |  |  | SERVER G DL360 (GEN8 OR GEN9) | [7 empty] | 32 | SERVER D DL380 (GEN8 OR GEN9) |  |  |  | SERVER G DL360 (GEN8 OR GEN9)
|  | 31 | (cxen3-bay9) BLADE | (cxen3-bay10) BLADE | (cxen3-bay11) BLADE | (cxen3-bay12) BLADE | (cxen3-bay13) BLADE | (cxen3-bay14) BLADE | (cxen3-bay15) BLADE | (cxen3-bay16) BLADE |  |  |  |  | 31 |  |  |  |  | SERVER H DL360 (GEN8 OR GEN9) | [7 empty] | 31 |  |  |  |  | SERVER H DL360 (GEN8 OR GEN9)
|  | 33 32: 30 |  |  |  |  | 30 | SERVER E DL380 (GEN8 OR GEN9) |  |  |  | SERVER I DL360 (GEN8 OR GEN9) | [7 empty] | 30 | SERVER E DL380 (GEN8 OR GEN9) |  |  |  | SERVER I DL360 (GEN8 OR GEN9)
|  | 33 32: 29 |  |  |  |  | 29 |  |  |  |  | SERVER J DL360 (GEN8 OR GEN9) | [7 empty] | 29 |  |  |  |  | SERVER J DL360 (GEN8 OR GEN9)
A1-5 EXT. BAR | A1-6 EXT. BAR | 33 32: 28 | B1-6 EXT. BAR | B1-5 EXT. BAR | A1-5 EXT. BAR | A1-6 EXT. BAR | 28 | SERVER F DL380 (GEN8 OR GEN9) |  |  |  | SERVER K DL360 (GEN8 OR GEN9) |  |  |  | B1-6 EXT. BAR | B1-5 EXT. BAR | A1-5 EXT. BAR | A1-6 EXT. BAR | 28 | SERVER F DL380 (GEN8 OR GEN9) |  |  |  | SERVER K DL360 (GEN8 OR GEN9) |  |  |  | B1-6 EXT. BAR | B1-5 EXT. BAR
|  | 27 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 27 |  |  |  |  | SERVER L DL360 (GEN8 OR GEN9) | [7 empty] | 27 |  |  |  |  | SERVER L DL360 (GEN8 OR GEN9)
|  | 26 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE |  |  |  |  | 26 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE |  |  |  |  | 26 | SERVER G DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 28 27: 25 |  |  |  |  | 25 | [12 empty] | 25 |  |  |  |  | FILLER PANEL
|  | 28 27: 24 |  |  |  |  | 24 | [12 empty] | 24 | SERVER H DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 28 27: 23 |  |  |  |  | 23 | [12 empty] | 23 |  |  |  |  | FILLER PANEL
|  | 22 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  | A1-4 EXT. BAR | 22 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | B1-4 EXT. BAR |  |  | A1-4 EXT. BAR | 22 | SERVER I DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL |  |  |  | B1-4 EXT. BAR
|  | 21 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE |  |  |  |  | 21 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE |  |  |  |  | 21 |  |  |  |  | FILLER PANEL
|  | 23 22: 20 |  |  |  |  | 20 | [12 empty] | 20 | SERVER J DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 23 22: 19 |  |  |  |  | 19 | [12 empty] | 19 |  |  |  |  | FILLER PANEL
|  | 23 22: 18 |  |  |  |  | 18 | [12 empty] | 18 | SERVER K DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 17 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 17 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 17 |  |  |  |  | FILLER PANEL
|  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 16 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 18 17: 15 |  |  |  |  | 15 | [12 empty] | 15
|  | 18 17: 14 |  |  |  |  | 14 | [12 empty] | 14
|  | 18 17: 13 |  |  |  |  | 13 | [12 empty] | 13
|  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 11 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 13 12: 10 |  |  |  |  | 10 | [12 empty] | 10
|  | 13 12: 9 |  |  |  |  | 9 | [12 empty] | 9
|  | 13 12: 8 |  |  |  |  | 8 | [12 empty] | 8
|  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 8 7: 6; 8 9: FILLER PANEL | HP PN BW929A (Filler Panel Pack of 100) (REF) |  |  |  | 6 | FILLER PANEL | [8 empty] | HP PN BW929A (Filler Panel Pack of 100) (REF) |  |  | 6 | FILLER PANEL
|  | 8 7: 5; 8 9: FILLER PANEL |  |  |  |  | 5 | FILLER PANEL | [11 empty] | 5 | FILLER PANEL
|  | 8 7: 4; 8 9: PDU B2 |  |  |  |  | 4 | PDU B2 | [11 empty] | 4 | FILLER PANEL
|  | 8 7: 3; 8 9: PDU A2 |  |  |  |  | 3 | PDU A2 | [11 empty] | 3 | FILLER PANEL
|  | 8 7: 2; 8 9: PDU B1 |  |  |  |  | 2 | PDU B1 | [11 empty] | 2 | PDU B1
|  | 8 7: 1; 8 9: PDU A1 |  |  |  |  | 1 | PDU A1 | [11 empty] | 1 | PDU A1
NOTE 1: THE GEN8 AND GEN9 SERVERS CAN BE MIXED IN THE SAME CABINET. THE SERVERS SHOWN ABOVE IN FIGURE 1D, 1E AND 1F COULD BE DL380 GEN8 SERVERS OR THE HP DL380 GEN9 SERVER. BOTH SERVERS ARE 2U SERVER SO THERE IS NOT RESTRICTIONS FOR INSTALLING A HP DL380 GEN9 SERVER IN ANY AVAILABLE SERVER POSITION. ALL SERVERS ARE FRONT MOUNTED AND THE 4948E-F SWITCHES WILL BE REAR MOUNTED. PDUS ARE FRONT MOUNTED. INSTALL THE PANDUIT AIR DUCT FOR SWITCH "A" IN U39-U40 AND THE AIR DUCT FOR SWITCH B IN U41-U42. AIR DUCT IS 2U HIGH AND THE AIR INTAKE GRILL SHOULD BE MOUNTED IN THE FRONT OF THE CABINET. THE SWITCHES WILL MOUNT IN THE AIR DUCT WITH THE ETHERNET PORTS FACING THE REAR OF THE CABINET, SEE PANDUIT ASSEMBLY INSTRUCTIONS AND FIGURE 2 AND 3. THE CABLE MANAGEMENT BARS ARE INCLUDED IN THE 814-0033-02 ASSEMBLY MATERIALS KIT. MOUNT THE CABLE MANAGEMENT BARS TO THE REAR OF THE CABINET TO THE AIR DUCT MOUNTING BRACKET SEE FIGURE 3. THE 2U SERVERS CAN BE EITHER HP DL380 OR NETRA X3-2 (SEE PICK LIST FOR DETAILS). FILLER PANELS IN ALL OPEN U LOCATIONS (SEE ASSEMBLY NOTES 6,7,8,9,10,11 AND 17).
SWITCH A
SWITCH A
SWITCH A
SWITCH B
SWITCH B
SWITCH B

## 870-3103-01_WL_GEN9_Cab Layout
FIGURE 1N: 870-3103-01 in the 805-0585-01 WRIGHT LINE CABINET (44U) WITH GEN9 SERVERS AND BLADES (SEE NOTE 1 BELOW
|  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01 | [11 empty] | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
|  | 44 | [12 empty] | 44
|  | 43 | [12 empty] | 43
|  | 42 | [12 empty] | 42
|  | 41 | [12 empty] | 41
|  | 40 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9 | [7 empty] | 40 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9
|  | 39 |  |  |  |  | SERVER B DL360 GEN9 | [7 empty] | 39 |  |  |  |  | SERVER B DL360 GEN9
LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) | 38 | SERVER B DL380 GEN9 |  |  |  | SERVER C DL360 GEN9 |  |  |  | PDU B PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) |  |  | PDU A PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) | 38 | SERVER B DL380 GEN9 |  |  |  | SERVER C DL360 GEN9 |  |  |  | PDU B PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item)
|  | 37 |  |  |  |  | SERVER D DL360 GEN9 | [7 empty] | 37 |  |  |  |  | FILLER PANEL
|  | 36 | SERVER C DL380 GEN9 |  |  |  | SERVER E DL360 GEN9 | [7 empty] | 36 | SERVER C DL380 GEN9 |  |  |  | FILLER PANEL
|  | 35 |  |  |  |  | SERVER F DL360 GEN9 | [7 empty] | 35 |  |  |  |  | FILLER PANEL
|  | 34 | SERVER D DL380 GEN9 |  |  |  | SERVER G DL360 GEN9 | [7 empty] | 34 | FILLER PANEL
|  | 33 |  |  |  |  | SERVER H DL360 GEN9 | [7 empty] | 33 | FILLER PANEL
|  | 32 | SERVER E DL380 GEN9 |  |  |  | SERVER I DL360 GEN9 | [7 empty] | 32 | FILLER PANEL
|  | 31 |  |  |  |  | SERVER J DL360 GEN9 | [7 empty] | 31 | FILLER PANEL
|  | 30 | SERVER F DL380 GEN9 |  |  |  | SERVER K DL360 GEN9 | [7 empty] | 30 | FILLER PANEL | [8 empty] | LOCATE PDU A AND B APPROX BETWEEN U38/39
|  | 29 |  |  |  |  | SERVER L DL360 GEN9 | [7 empty] | 29 | FILLER PANEL
|  | 28 | SERVER G DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 28 | FILLER PANEL
|  | 27 |  |  |  |  | FILLER PANEL | [7 empty] | 27 | FILLER PANEL
|  | 26 | SERVER H DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 26 | FILLER PANEL
|  | 25 |  |  |  |  | FILLER PANEL | [7 empty] | 25 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace
|  | 24 | SERVER I DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 24 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE
|  | 23 |  |  |  |  | FILLER PANEL | [7 empty] | 23
|  | 22 | SERVER J DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 22
|  | 21 |  |  |  |  | FILLER PANEL | [7 empty] | 21
|  | 20 | SERVER K DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 20 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 19 |  |  |  |  | FILLER PANEL | [7 empty] | 19 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE
|  | 18 | SERVER L DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 21 20: 18
|  | 17 |  |  |  |  | FILLER PANEL | [7 empty] | 21 20: 17
|  | 16 | FILLER PANEL | [11 empty] | 21 20: 16
|  | 15 | FILLER PANEL | [11 empty] | 15 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 14 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace |  |  | 16 15: 14; 16 9: SEISMIC BRACE 805-0188-GXX |  | Seismic Brace
|  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 12 | [12 empty] | 16 15: 12
|  | 11 | [12 empty] | 16 15: 11
|  | 10 | [12 empty] | 16 15: 10
|  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 10 9: 7 |  |  |  |  | 7
|  | 10 9: 6 |  |  |  |  | 6
|  | 10 9: 5 |  |  |  |  | 5
|  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 5 4: 3; 5 9: FILLER PANEL |  |  |  |  | 3 | FILLER PANEL
|  | 5 4: 2; 5 9: FILLER PANEL |  |  |  |  | 2 | FILLER PANEL
|  | 5 4: 1; 5 9: FILLER PANEL |  |  |  |  | 1 | FILLER PANEL
FRONT VIEW 805-0585-01 WRIGHT LINE CABINET (44U) with one enclosure | [12 empty] | FRONT VIEW 805-0585-01 WRIGHT LINE CABINET (44U) with two enclosures
FIGURE 1P: 870-3103-01 in the 805-0583-01 WRIGHT LINE CABINET (40U) WITH GEN9 SERVERS AND BLADES (SEE NOTE 1 BELOW)
|  | 5 4: RACK U; 5 9: Eagle XG c-Class Cabinet (Max config) 870-3103-01 |  |  |  |  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
|  | 5 4: 40 |  |  |  |  | 40
|  | 5 4: 39 |  |  |  |  | 39
LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) | 5 4: 38 | PDU B PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) |  | LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) | 38 | [8 empty] | PDU B PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item)
|  | 5 4: 37 |  |  |  |  | 37
|  | 5 4: 36; 5 9: SERVER A DL380 GEN9; 5 13: SERVER A DL360 GEN9 |  |  |  |  | 36 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9
|  | 5 4: 35; 5 13: SERVER B DL360 GEN9 |  |  |  |  | 35 |  |  |  |  | SERVER B DL360 GEN9
|  | 5 4: 34; 5 9: SERVER B DL380 GEN9; 5 13: SERVER C DL360 GEN9 |  |  |  |  | 34 | SERVER B DL380 GEN9 |  |  |  | SERVER C DL360 GEN9
|  | 5 4: 33; 5 13: SERVER D DL360 GEN9 |  |  |  |  | 33 |  |  |  |  | FILLER PANEL
|  | 5 4: 32; 5 9: SERVER C DL380 GEN9; 5 13: SERVER E DL360 GEN9 |  |  |  |  | 32 | SERVER C DL380 GEN9 |  |  |  | FILLER PANEL
|  | 5 4: 31; 5 13: SERVER F DL360 GEN9 |  |  |  |  | 31 |  |  |  |  | FILLER PANEL
|  | 5 4: 30; 5 9: SERVER D DL380 GEN9; 5 13: SERVER G DL360 GEN9 |  |  |  |  | 30 | FILLER PANEL
|  | 5 4: 29; 5 13: SERVER H DL360 GEN9 |  |  |  |  | 29 | FILLER PANEL
|  | 5 4: 28; 5 9: SERVER E DL380 GEN9; 5 13: SERVER I DL360 GEN9 |  |  |  |  | 28 | FILLER PANEL
|  | 5 4: 27; 5 13: SERVER J DL360 GEN9 |  |  |  |  | 27 | FILLER PANEL
|  | 5 4: 26; 5 9: SERVER F DL380 GEN9; 5 13: SERVER K DL360 GEN9 |  |  |  |  | 26 | FILLER PANEL
|  | 5 4: 25; 5 13: SERVER L DL360 GEN9 |  | Seismic Brace (NOTE 7 below) |  |  | 25 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace
|  | 5 4: 24; 5 9: SERVER G DL380 GEN9; 5 13: FILLER PANEL |  |  |  |  | 24 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE
|  | 5 4: 23; 5 13: FILLER PANEL |  |  |  |  | 23
|  | 5 4: 22; 5 9: SERVER H DL380 GEN9; 5 13: FILLER PANEL |  |  |  |  | 22
|  | 5 4: 21; 5 13: FILLER PANEL |  |  |  |  | 21
|  | 20 | SERVER I DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 20 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 19 |  |  |  |  | FILLER PANEL | [7 empty] | 19 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE
|  | 18 | SERVER J DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 21 20: 18
|  | 17 |  |  |  |  | FILLER PANEL | [7 empty] | 21 20: 17
|  | 16 | SERVER K DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 21 20: 16
|  | 15 |  |  |  |  | FILLER PANEL | [7 empty] | 15 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 14 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace |  |  | 16 15: 14; 16 9: SEISMIC BRACE 805-0188-GXX |  | Seismic Brace
|  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 12 | [12 empty] | 16 15: 12
|  | 11 | [12 empty] | 16 15: 11
|  | 10 | [12 empty] | 16 15: 10
|  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 10 9: 7 |  |  |  |  | 7
|  | 10 9: 6 |  |  |  |  | 6
|  | 10 9: 5 |  |  |  |  | 5
|  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 5 4: 3; 5 9: FILLER PANEL |  |  |  |  | 3 | FILLER PANEL
|  | 5 4: 2; 5 9: FILLER PANEL |  |  |  |  | 2 | FILLER PANEL
|  | 5 4: 1; 5 9: FILLER PANEL |  |  |  |  | 1 | FILLER PANEL
FRONT VIEW 805-0583-01 WRIGHT LINE CABINET (40U) with one enclosure | [12 empty] | FRONT VIEW 805-0583-01 WRIGHT LINE CABINET (40U) with two enclosures
FIGURE 1R: 870-3103-01 in the 805-0582-01 WRIGHT LINE CABINET (44U) WITH GEN9 SERVERS AND BLADES (SEE NOTE 1 BELOW)
|  | 5 4: RACK U; 5 9: Eagle XG c-Class Cabinet (Max config) 870-3103-01 |  |  |  |  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
|  | 5 4: 44 |  |  |  |  | 44
Switch B |  | 5 4: 43 |  |  | Switch B |  | 43
|  | 5 4: 42 |  |  |  |  | 42
Switch A |  | 5 4: 41 |  |  | Switch A |  | 41
|  | 5 4: 40; 5 9: SERVER A DL380 GEN9; 5 13: SERVER A DL360 GEN9 |  |  |  |  | 40 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9
|  | 5 4: 39; 5 13: SERVER B DL360 GEN9 |  |  |  |  | 39 |  |  |  |  | SERVER B DL360 GEN9
LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0582-01) | 5 4: 38; 5 9: SERVER B DL380 GEN9; 5 13: SERVER C DL360 GEN9 | PDU B WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0582-01) |  | LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0582-01) | 38 | SERVER B DL380 GEN9 |  |  |  | SERVER C DL360 GEN9 |  |  |  | PDU B WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0582-01)
|  | 5 4: 37; 5 13: SERVER D DL360 GEN9 |  |  |  |  | 37 |  |  |  |  | FILLER PANEL
|  | 5 4: 36; 5 9: SERVER C DL380 GEN9; 5 13: SERVER E DL360 GEN9 |  |  |  |  | 36 | SERVER C DL380 GEN9 |  |  |  | FILLER PANEL
|  | 5 4: 35; 5 13: SERVER F DL360 GEN9 |  |  |  |  | 35 |  |  |  |  | FILLER PANEL
|  | 5 4: 34; 5 9: SERVER D DL380 GEN9; 5 13: SERVER G DL360 GEN9 |  |  |  |  | 34 | FILLER PANEL
|  | 5 4: 33; 5 13: SERVER H DL360 GEN9 |  |  |  |  | 33 | FILLER PANEL
|  | 5 4: 32; 5 9: SERVER E DL380 GEN9; 5 13: SERVER I DL360 GEN9 |  |  |  |  | 32 | FILLER PANEL
|  | 5 4: 31; 5 13: SERVER J DL360 GEN9 |  |  |  |  | 31 | FILLER PANEL
|  | 5 4: 30; 5 9: SERVER F DL380 GEN9; 5 13: SERVER K DL360 GEN9 |  |  |  |  | 30 | FILLER PANEL
|  | 5 4: 29; 5 13: SERVER L DL360 GEN9 |  |  |  |  | 29 | FILLER PANEL
|  | 5 4: 28; 5 9: SERVER G DL380 GEN9; 5 13: FILLER PANEL |  |  |  |  | 28 | FILLER PANEL
|  | 5 4: 27; 5 13: FILLER PANEL |  |  |  |  | 27 | FILLER PANEL
|  | 5 4: 26; 5 9: SERVER H DL380 GEN9; 5 13: FILLER PANEL |  |  |  |  | 26 | FILLER PANEL
|  | 5 4: 25; 5 13: FILLER PANEL |  |  |  |  | 25 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace
|  | 5 4: 24; 5 9: SERVER I DL380 GEN9; 5 13: FILLER PANEL |  |  |  |  | 24 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE
|  | 5 4: 23; 5 13: FILLER PANEL |  |  |  |  | 23
|  | 5 4: 22; 5 9: SERVER J DL380 GEN9; 5 13: FILLER PANEL |  |  |  |  | 22
|  | 5 4: 21; 5 13: FILLER PANEL |  |  |  |  | 21
|  | 20 | SERVER K DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 20 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 19 |  |  |  |  | FILLER PANEL | [7 empty] | 19 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE
|  | 18 | SERVER L DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 21 20: 18
|  | 17 |  |  |  |  | FILLER PANEL | [7 empty] | 21 20: 17
|  | 16 | FILLER PANEL | [11 empty] | 21 20: 16
|  | 15 | FILLER PANEL | [11 empty] | 15 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 14 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace |  |  | 16 15: 14; 16 9: SEISMIC BRACE 805-0188-GXX |  | Seismic Brace
|  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 12 | [12 empty] | 16 15: 12
|  | 11 | [12 empty] | 16 15: 11
|  | 10 | [12 empty] | 16 15: 10
|  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 10 9: 7 |  |  |  |  | 7
|  | 10 9: 6 |  |  |  |  | 6
|  | 10 9: 5 |  |  |  |  | 5
|  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 5 4: 3; 5 9: FILLER PANEL |  |  |  |  | 3 | FILLER PANEL
|  | 5 4: 2; 5 9: FILLER PANEL |  |  |  |  | 2 | FILLER PANEL
|  | 5 4: 1; 5 9: FILLER PANEL |  |  |  |  | 1 | FILLER PANEL
| FRONT VIEW 805-0582-01 WRIGHT LINE CABINET (44U) | [12 empty] | FRONT VIEW 805-0582-01 WRIGHT LINE CABINET (44U)
FIGURE 1S: 870-3103-01 in the 805-0562-01 WRIGHT LINE CABINET (40U) WITH GEN9 SERVERS AND BLADES (SEE NOTE 1 BELOW)
|  | 5 4: RACK U; 5 9: Eagle XG c-Class Cabinet (Max config) 870-3103-01 |  |  |  |  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
|  | 5 4: 40 |  |  |  |  | 40
|  | 5 4: 39 |  |  |  |  | 39
LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0562-01) | 5 4: 38 | PDU B WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0562-01) |  | LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0562-01) | 38 | [8 empty] | PDU B WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0562-01)
|  | 5 4: 37 |  |  |  |  | 37
|  | 5 4: 36; 5 9: SERVER A DL380 GEN9; 5 13: SERVER A DL360 GEN9 |  |  |  |  | 36 | SERVER A DL380 GEN9 |  |  |  | SERVER A DL360 GEN9
|  | 5 4: 35; 5 13: SERVER B DL360 GEN9 |  |  |  |  | 35 |  |  |  |  | SERVER B DL360 GEN9
|  | 5 4: 34; 5 9: SERVER B DL380 GEN9; 5 13: SERVER C DL360 GEN9 |  |  |  |  | 34 | SERVER B DL380 GEN9 |  |  |  | SERVER C DL360 GEN9
|  | 5 4: 33; 5 13: SERVER D DL360 GEN9 |  |  |  |  | 33 |  |  |  |  | FILLER PANEL
|  | 5 4: 32; 5 9: SERVER C DL380 GEN9; 5 13: SERVER E DL360 GEN9 |  |  |  |  | 32 | SERVER C DL380 GEN9 |  |  |  | FILLER PANEL
|  | 5 4: 31; 5 13: SERVER F DL360 GEN9 |  |  |  |  | 31 |  |  |  |  | FILLER PANEL
|  | 5 4: 30; 5 9: SERVER D DL380 GEN9; 5 13: SERVER G DL360 GEN9 |  |  |  |  | 30 | FILLER PANEL
|  | 5 4: 29; 5 13: SERVER H DL360 GEN9 |  |  |  |  | 29 | FILLER PANEL
|  | 5 4: 28; 5 9: SERVER E DL380 GEN9; 5 13: SERVER I DL360 GEN9 |  |  |  |  | 28 | FILLER PANEL
|  | 5 4: 27; 5 13: SERVER J DL360 GEN9 |  |  |  |  | 27 | FILLER PANEL
|  | 5 4: 26; 5 9: SERVER F DL380 GEN9; 5 13: SERVER K DL360 GEN9 |  |  |  |  | 26 | FILLER PANEL
|  | 5 4: 25; 5 13: SERVER L DL360 GEN9 |  |  |  |  | 25 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace
|  | 5 4: 24; 5 9: SERVER G DL380 GEN9; 5 13: FILLER PANEL |  |  |  |  | 24 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE
|  | 5 4: 23; 5 13: FILLER PANEL |  |  |  |  | 23
|  | 5 4: 22; 5 9: SERVER H DL380 GEN9; 5 13: FILLER PANEL |  |  |  |  | 22
|  | 5 4: 21; 5 13: FILLER PANEL |  |  |  |  | 21
|  | 20 | SERVER I DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 20 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 19 |  |  |  |  | FILLER PANEL | [7 empty] | 19 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE
|  | 18 | SERVER J DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 21 20: 18
|  | 17 |  |  |  |  | FILLER PANEL | [7 empty] | 21 20: 17
|  | 16 | SERVER K DL380 GEN9 |  |  |  | FILLER PANEL | [7 empty] | 21 20: 16
|  | 15 |  |  |  |  | FILLER PANEL | [7 empty] | 15 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 14 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace |  |  | 16 15: 14; 16 9: SEISMIC BRACE 805-0188-GXX |  | Seismic Brace
|  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 12 | [12 empty] | 16 15: 12
|  | 11 | [12 empty] | 16 15: 11
|  | 10 | [12 empty] | 16 15: 10
|  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 10 9: 7 |  |  |  |  | 7
|  | 10 9: 6 |  |  |  |  | 6
|  | 10 9: 5 |  |  |  |  | 5
|  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 5 4: 3; 5 9: FILLER PANEL |  |  |  |  | 3 | FILLER PANEL
|  | 5 4: 2; 5 9: FILLER PANEL |  |  |  |  | 2 | FILLER PANEL
|  | 5 4: 1; 5 9: FILLER PANEL |  |  |  |  | 1 | FILLER PANEL
| FRONT VIEW 805-0562-01 WRIGHT LINE CABINET (40U) | [12 empty] | FRONT VIEW 805-0562-01 WRIGHT LINE CABINET (40U)
NOTE 1: THE 870-3103-01 ASSEMBLY SHOWN ABOVE IN FIGURES 1N, 1P, 1R AND 1S ARE IN THE WRIGHT LINE CABINETS SUPPORTING BOTH 40U AND 44U TALL CABINETS (SHOWN FOR REFERENCE ONLY SEE ASSEMBLY NOTE 31) WITH GEN9 SERVERS AND BLADES. ALL ENCLOSURES AND SERVERS ARE FRONT MOUNTED AND THE 4948E-F SWITCHES WILL BE REAR MOUNTED USING THE PANDUIT AIR DUCT. THE AIR DUCT IS 2U HIGH AND THE AIR INTAKE GRILL SHOULD BE MOUNTED IN THE FRONT OF THE CABINET. THE SWITCHES WILL MOUNT IN THE AIR DUCT WITH THE ETHERNET PORTS FACING THE REAR OF THE CABINET, SEE PANDUIT ASSEMBLY INSTRUCTIONS AND FIGURE 3. THE CABLE MANAGEMENT BARS ARE INCLUDED IN THE SWITCH ASSEMBLY MATERIALS KIT. MOUNT THE CABLE MANAGEMENT BARS TO THE REAR OF THE CABINET TO THE AIR DUCT MOUNTING BRACKET SEE FIGURE 4. INSTALL FILLER PANELS IN ALL OPEN U LOCATIONS. SEE REFERENCE 21- TR007457 FOR DL380 GEN9 BLADE/SERVER CONFIGS. THE PICKLIST IN THIS DOCUMENT SUPPORTS THIS CABINET CONFIGURATION. SEE ASSEMBLY NOTE 28 TO DETERMINE WHAT ORDER TO INSTALL THE SERVERS IN THE CABINET. (SEE ASSEMBLY NOTES 6,7,8,9,10,11,17, 28 AND 31).
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure.
NETWORK ZONE (U41-U44)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
NETWORK ZONE (U37-U40)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
Zone 2 (U15-U25)
2nd c7000 enclosure (cxen2) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure.
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure.
Zone 2 (U15-U25)
2nd c7000 enclosure (cxen2) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure.
Zone 3 (U26-U36)
3 x 1U serves (HP DL360 GEN9) or 3 x 2U servers (HP DL380 GEN9) if 2nd c7000 enclosure (cxen2) is installed. Install filler panels if open in front of cabinet.
NETWORK ZONE (U41-U44)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) 805-0592-02
(Mount switch in the Panduit Air Duct PN 805-0593-01)
Zone 3 (U26-U40)
15U Reserved for Server A through Server C
3 DL360 GEN9 servers or 3 DL380 GEN9 servers if 2nd c7000 enclosure (cxen2) is installed. Install filler panels if open in front of cabinet
Zone 2 (U15-U25)
2nd c7000 enclosure (cxen2) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
NETWORK ZONE (U37-U40)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) 805-0592-02
(Mount switch in the Panduit Air Duct PN 805-0593-01)
Zone 3 (U26-U36)
3 DL360 GEN9 servers or 3 DL380 GEN9 servers if 2nd c7000 enclosure (cxen2) is installed. Install filler panels if open in front of cabinet
Zone 2 (U15-U25)
2nd c7000 enclosure (cxen2) 805-0540-GXX
See Figure 1E and Assy Note 25 for guidelines on Blade placement in c7000 enclosure
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure.
Zone 2 and Zone 3 (U15-U36)
12 x 1U servers (HP DL360 GEN9) or 11 x 2U serves (HP DL380 GEN9) is supported if the 2nd c7000 enclosure (cxen2) is not installed. Install filler panels if open in front of cabinet.
Zone 2 and Zone 3 (U15-U40)
12 x 1U servers (HP DL360 GEN9) or 12 x 2U servers (HP DL380 GEN9) if the 2nd c7000 enclosure (cxen2) is not installed. Install filler panels if open in front of cabinet.
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
Zone 2 and Zone 3 (U15-U40)
12 DL360 GEN9 servers or 11 DL380 GEN9 if the 2nd c7000 enclosure (cxen2) is not installed. Install filler panels if open in front of cabinet.
NETWORK ZONE (U37-U40)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
Zone 2 and 3 (U15-U36)
12 DL360 GEN9 servers or 11 DL380 GEN9 servers if the 2nd c7000 enclosure (cxen2) is not installed. Install filler panels if open in front of cabinet.
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
NETWORK ZONE (U37-U40)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
NETWORK ZONE (U41-U44)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted)
PN 805-0592-02
(Mount switch in the Panduit Air Duct
PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted)
PN 805-0592-02
(Mount switch in the Panduit Air Duct
PN 805-0593-01)
Zone 3 (U26-U40)
3 x 1U servers (HP DL360 GEN9 ) or 3 x 2U servers (HP DL380 GEN9) if 2nd c7000 enclosure (cxen2) is installed. Install filler panels if open in front of cabinet.
NETWORK ZONE (U37-U40)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted)
PN 805-0592-02
(Mount switch in the Panduit Air Duct
PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted)
PN 805-0592-02
(Mount switch in the Panduit Air Duct
PN 805-0593-01)
870-3103-01_WL_GEN9 Cabinet Layout Tab
Install filler panels in all open spaces as shown
all open "U" locations should be filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
all open "U" locations should be filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
all open "U" locations should be filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
all open "U" locations should be filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
all open "U" locations should be filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
all open "U" locations should be filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
all open "U" locations should be filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
all open "U" locations should be filled with a filler panel. See 870-3103-01 picklist for filler panel part number.

## 870-3103-01_WL_GEN8_GEN9_Cab La
FIGURE 1T: 870-3103-01 in the 805-0585-01 WRIGHT LINE CABINET (44U) COMINGLED WITH GEN9 AND GEN8 SERVERS AND BLADES (SEE NOTE 1 BELOW AND ASSEMBLY NOTE 32)
|  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01 | [11 empty] | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
|  | 44 | [12 empty] | 44
|  | 43 | [12 empty] | 43
|  | 42 | [12 empty] | 42
|  | 41 | [12 empty] | 41
|  | 40 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9) | [7 empty] | 40 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9)
|  | 39 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9) | [7 empty] | 39 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9)
LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) | 38 | SERVER B DL380 (GEN8 OR GEN9) |  |  |  | SERVER C DL360 (GEN8 OR GEN9) |  |  |  | PDU B PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) |  |  | PDU A PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) | 38 | SERVER B DL380 (GEN8 OR GEN9) |  |  |  | SERVER C DL360 (GEN8 OR GEN9) |  |  |  | PDU B PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item)
|  | 37 |  |  |  |  | SERVER D DL360 (GEN8 OR GEN9) | [7 empty] | 37 |  |  |  |  | FILLER PANEL
|  | 36 | SERVER C DL380 (GEN8 OR GEN9) |  |  |  | SERVER E DL360 (GEN8 OR GEN9) | [7 empty] | 36 | SERVER C DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 35 |  |  |  |  | SERVER F DL360 (GEN8 OR GEN9) | [7 empty] | 35 |  |  |  |  | FILLER PANEL
|  | 34 | SERVER D DL380 (GEN8 OR GEN9) |  |  |  | SERVER G DL360 (GEN8 OR GEN9) | [7 empty] | 34 | FILLER PANEL
|  | 33 |  |  |  |  | SERVER H DL360 (GEN8 OR GEN9) | [7 empty] | 33 | FILLER PANEL
|  | 32 | SERVER E DL380 (GEN8 OR GEN9) |  |  |  | SERVER I DL360 (GEN8 OR GEN9) | [7 empty] | 32 | FILLER PANEL
|  | 31 |  |  |  |  | SERVER J DL360 (GEN8 OR GEN9) | [7 empty] | 31 | FILLER PANEL
|  | 30 | SERVER F DL380 (GEN8 OR GEN9) |  |  |  | SERVER K DL360 (GEN8 OR GEN9) | [7 empty] | 30 | FILLER PANEL | [8 empty] | LOCATE PDU A AND B APPROX BETWEEN U38/39
|  | 29 |  |  |  |  | SERVER L DL360 (GEN8 OR GEN9) | [7 empty] | 29 | FILLER PANEL
|  | 28 | SERVER G DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 28 | FILLER PANEL
|  | 27 |  |  |  |  | FILLER PANEL | [7 empty] | 27 | FILLER PANEL
|  | 26 | SERVER H DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 26 | FILLER PANEL
|  | 25 |  |  |  |  | FILLER PANEL | [7 empty] | 25 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace
|  | 24 | SERVER I DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 24 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE
|  | 23 |  |  |  |  | FILLER PANEL | [7 empty] | 23
|  | 22 | SERVER J DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 22
|  | 21 |  |  |  |  | FILLER PANEL |  |  |  |  | LOCATE PDU A AND B APPROX BETWEEN U38/39 |  |  | 21
|  | 20 | SERVER K DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 20 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 19 |  |  |  |  | FILLER PANEL | [7 empty] | 19 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE
|  | 18 | SERVER L DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 21 20: 18
|  | 17 |  |  |  |  | FILLER PANEL | [7 empty] | 21 20: 17
|  | 16 | FILLER PANEL | [11 empty] | 21 20: 16
|  | 15 | FILLER PANEL | [11 empty] | 15 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 14 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace |  |  | 16 15: 14; 16 9: SEISMIC BRACE 805-0188-GXX |  | Seismic Brace
|  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 12 | [12 empty] | 16 15: 12
|  | 11 | [12 empty] | 16 15: 11
|  | 10 | [12 empty] | 16 15: 10
|  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 10 9: 7 |  |  |  |  | 7
|  | 10 9: 6 |  |  |  |  | 6
|  | 10 9: 5 |  |  |  |  | 5
|  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 5 4: 3; 5 9: FILLER PANEL |  |  |  |  | 3 | FILLER PANEL
|  | 5 4: 2; 5 9: FILLER PANEL |  |  |  |  | 2 | FILLER PANEL
|  | 5 4: 1; 5 9: FILLER PANEL |  |  |  |  | 1 | FILLER PANEL
FRONT VIEW 805-0585-01 WRIGHT LINE CABINET (44U) with one enclosure | [12 empty] | FRONT VIEW 805-0585-01 WRIGHT LINE CABINET (44U) with two enclosures
FIGURE 1W: 870-3103-01 in the 805-0583-01 WRIGHT LINE CABINET (40U)COMINGLED WITH GEN9 AND GEN8 SERVERS AND BLADES (SEE NOTE 1 BELOW AND ASSEMBLY NOTE 32)
|  | 5 4: RACK U; 5 9: Eagle XG c-Class Cabinet (Max config) 870-3103-01 |  |  |  |  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
|  | 5 4: 40 |  |  |  |  | 40
|  | 5 4: 39 |  |  |  |  | 39
LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) | 5 4: 38 | PDU B PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) |  | LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item) | 38 | [8 empty] | PDU B PN 805-0584-01 or 7095212 - 50A, 3 Phase PDU (Orderable Item)
|  | 5 4: 37 |  |  |  |  | 37
|  | 5 4: 36; 5 9: SERVER A DL380 (GEN8 OR GEN9); 5 13: SERVER A DL360 (GEN8 OR GEN9) |  |  |  |  | 36 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9)
|  | 5 4: 35; 5 13: SERVER B DL360 (GEN8 OR GEN9) |  |  |  |  | 35 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9)
|  | 5 4: 34; 5 9: SERVER B DL380 (GEN8 OR GEN9); 5 13: SERVER C DL360 (GEN8 OR GEN9) |  |  |  |  | 34 | SERVER B DL380 (GEN8 OR GEN9) |  |  |  | SERVER C DL360 (GEN8 OR GEN9)
|  | 5 4: 33; 5 13: SERVER D DL360 (GEN8 OR GEN9) |  |  |  |  | 33 |  |  |  |  | FILLER PANEL
|  | 5 4: 32; 5 9: SERVER C DL380 (GEN8 OR GEN9); 5 13: SERVER E DL360 (GEN8 OR GEN9) |  |  |  |  | 32 | SERVER C DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 5 4: 31; 5 13: SERVER F DL360 (GEN8 OR GEN9) |  |  |  |  | 31 |  |  |  |  | FILLER PANEL
|  | 5 4: 30; 5 9: SERVER D DL380 (GEN8 OR GEN9); 5 13: SERVER G DL360 (GEN8 OR GEN9) |  |  |  |  | 30 | FILLER PANEL
|  | 5 4: 29; 5 13: SERVER H DL360 (GEN8 OR GEN9) |  |  |  |  | 29 | FILLER PANEL
|  | 5 4: 28; 5 9: SERVER E DL380 (GEN8 OR GEN9); 5 13: SERVER I DL360 (GEN8 OR GEN9) |  |  |  |  | 28 | FILLER PANEL
|  | 5 4: 27; 5 13: SERVER J DL360 (GEN8 OR GEN9) |  |  |  |  | 27 | FILLER PANEL
|  | 5 4: 26; 5 9: SERVER F DL380 (GEN8 OR GEN9); 5 13: SERVER K DL360 (GEN8 OR GEN9) |  |  |  |  | 26 | FILLER PANEL
|  | 5 4: 25; 5 13: SERVER L DL360 (GEN8 OR GEN9) |  | Seismic Brace (NOTE 7 below) |  |  | 25 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace
|  | 5 4: 24; 5 9: SERVER G DL380 (GEN8 OR GEN9); 5 13: FILLER PANEL |  |  |  |  | 24 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE
|  | 5 4: 23; 5 13: FILLER PANEL |  |  |  |  | 23
|  | 5 4: 22; 5 9: SERVER H DL380 (GEN8 OR GEN9); 5 13: FILLER PANEL |  |  |  |  | 22
|  | 5 4: 21; 5 13: FILLER PANEL |  |  |  |  | 21
|  | 20 | SERVER I DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 20 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 19 |  |  |  |  | FILLER PANEL | [7 empty] | 19 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE
|  | 18 | SERVER J DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 21 20: 18
|  | 17 |  |  |  |  | FILLER PANEL | [7 empty] | 21 20: 17
|  | 16 | SERVER K DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 21 20: 16
|  | 15 |  |  |  |  | FILLER PANEL | [7 empty] | 15 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 14 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace |  |  | 16 15: 14; 16 9: SEISMIC BRACE 805-0188-GXX |  | Seismic Brace
|  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 12 | [12 empty] | 16 15: 12
|  | 11 | [12 empty] | 16 15: 11
|  | 10 | [12 empty] | 16 15: 10
|  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 10 9: 7 |  |  |  |  | 7
|  | 10 9: 6 |  |  |  |  | 6
|  | 10 9: 5 |  |  |  |  | 5
|  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 5 4: 3; 5 9: FILLER PANEL |  |  |  |  | 3 | FILLER PANEL
|  | 5 4: 2; 5 9: FILLER PANEL |  |  |  |  | 2 | FILLER PANEL
|  | 5 4: 1; 5 9: FILLER PANEL |  |  |  |  | 1 | FILLER PANEL
FRONT VIEW 805-0583-01 WRIGHT LINE CABINET (40U) with one enclosure | [12 empty] | FRONT VIEW 805-0583-01 WRIGHT LINE CABINET (40U) with two enclosures
FIGURE 1X: 870-3103-01 in the 805-0582-01 WRIGHT LINE CABINET (44U) COMINGLED WITH GEN9 AND GEN8 SERVERS AND BLADES (SEE NOTE 1 BELOW AND ASSEMBLY NOTE 32)
|  | 5 4: RACK U; 5 9: Eagle XG c-Class Cabinet (Max config) 870-3103-01 |  |  |  |  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
|  | 5 4: 44 |  |  |  |  | 44
Switch B |  | 5 4: 43 |  |  | Switch B |  | 43
|  | 5 4: 42 |  |  |  |  | 42
Switch A |  | 5 4: 41 |  |  | Switch A |  | 41
|  | 5 4: 40; 5 9: SERVER A DL380 (GEN8 OR GEN9); 5 13: SERVER A DL360 (GEN8 OR GEN9) |  |  |  |  | 40 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9)
|  | 5 4: 39; 5 13: SERVER B DL360 (GEN8 OR GEN9) |  |  |  |  | 39 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9)
LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0582-01) | 5 4: 38; 5 9: SERVER B DL380 (GEN8 OR GEN9); 5 13: SERVER C DL360 (GEN8 OR GEN9) | PDU B WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0582-01) |  | LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0582-01) | 38 | SERVER B DL380 (GEN8 OR GEN9) |  |  |  | SERVER C DL360 (GEN8 OR GEN9) |  |  |  | PDU B WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0582-01)
|  | 5 4: 37; 5 13: SERVER D DL360 (GEN8 OR GEN9) |  |  |  |  | 37 |  |  |  |  | FILLER PANEL
|  | 5 4: 36; 5 9: SERVER C DL380 (GEN8 OR GEN9); 5 13: SERVER E DL360 (GEN8 OR GEN9) |  |  |  |  | 36 | SERVER C DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 5 4: 35; 5 13: SERVER F DL360 (GEN8 OR GEN9) |  |  |  |  | 35 |  |  |  |  | FILLER PANEL
|  | 5 4: 34; 5 9: SERVER D DL380 (GEN8 OR GEN9); 5 13: SERVER G DL360 (GEN8 OR GEN9) |  |  |  |  | 34 | FILLER PANEL
|  | 5 4: 33; 5 13: SERVER H DL360 (GEN8 OR GEN9) |  |  |  |  | 33 | FILLER PANEL
|  | 5 4: 32; 5 9: SERVER E DL380 (GEN8 OR GEN9); 5 13: SERVER I DL360 (GEN8 OR GEN9) |  |  |  |  | 32 | FILLER PANEL
|  | 5 4: 31; 5 13: SERVER J DL360 (GEN8 OR GEN9) |  |  |  |  | 31 | FILLER PANEL
|  | 5 4: 30; 5 9: SERVER F DL380 (GEN8 OR GEN9); 5 13: SERVER K DL360 (GEN8 OR GEN9) |  |  |  |  | 30 | FILLER PANEL
|  | 5 4: 29; 5 13: SERVER L DL360 (GEN8 OR GEN9) |  |  |  |  | 29 | FILLER PANEL
|  | 5 4: 28; 5 9: SERVER G DL380 (GEN8 OR GEN9); 5 13: FILLER PANEL |  |  |  |  | 28 | FILLER PANEL
|  | 5 4: 27; 5 13: FILLER PANEL |  |  |  |  | 27 | FILLER PANEL
|  | 5 4: 26; 5 9: SERVER H DL380 (GEN8 OR GEN9); 5 13: FILLER PANEL |  |  |  |  | 26 | FILLER PANEL
|  | 5 4: 25; 5 13: FILLER PANEL |  |  |  |  | 25 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace
|  | 5 4: 24; 5 9: SERVER I DL380 (GEN8 OR GEN9); 5 13: FILLER PANEL |  |  |  |  | 24 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE
|  | 5 4: 23; 5 13: FILLER PANEL |  |  |  |  | 23
|  | 5 4: 22; 5 9: SERVER J DL380 (GEN8 OR GEN9); 5 13: FILLER PANEL |  |  |  |  | 22
|  | 5 4: 21; 5 13: FILLER PANEL |  |  |  |  | 21
|  | 20 | SERVER K DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 20 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 19 |  |  |  |  | FILLER PANEL | [7 empty] | 19 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE
|  | 18 | SERVER L DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 21 20: 18
|  | 17 |  |  |  |  | FILLER PANEL | [7 empty] | 21 20: 17
|  | 16 | FILLER PANEL | [11 empty] | 21 20: 16
|  | 15 | FILLER PANEL | [11 empty] | 15 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 14 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace |  |  | 16 15: 14; 16 9: SEISMIC BRACE 805-0188-GXX |  | Seismic Brace
|  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 12 | [12 empty] | 16 15: 12
|  | 11 | [12 empty] | 16 15: 11
|  | 10 | [12 empty] | 16 15: 10
|  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 10 9: 7 |  |  |  |  | 7
|  | 10 9: 6 |  |  |  |  | 6
|  | 10 9: 5 |  |  |  |  | 5
|  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 5 4: 3; 5 9: FILLER PANEL |  |  |  |  | 3 | FILLER PANEL
|  | 5 4: 2; 5 9: FILLER PANEL |  |  |  |  | 2 | FILLER PANEL
|  | 5 4: 1; 5 9: FILLER PANEL |  |  |  |  | 1 | FILLER PANEL
| FRONT VIEW 805-0582-01 WRIGHT LINE CABINET (44U) | [12 empty] | FRONT VIEW 805-0582-01 WRIGHT LINE CABINET (44U)
FIGURE 1Y: 870-3103-01 in the 805-0562-01 WRIGHT LINE CABINET (40U) COMINGLED WITH GEN9 AND GEN8 SERVERS AND BLADES (SEE NOTE 1 BELOW AND ASSEMBLY NOTE 32)
|  | 5 4: RACK U; 5 9: Eagle XG c-Class Cabinet (Max config) 870-3103-01 |  |  |  |  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
|  | 5 4: 40 |  |  |  |  | 40
|  | 5 4: 39 |  |  |  |  | 39
LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0562-01) | 5 4: 38 | PDU B WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0562-01) |  | LOCATE PDU A AND B APPROX BETWEEN U38/39 | PDU A WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0562-01) | 38 | [8 empty] | PDU B WRIGHT LINE PN 17110217_30A, 3 Phase PDU (Part of 805-0562-01)
|  | 5 4: 37 |  |  |  |  | 37
|  | 5 4: 36; 5 9: SERVER A DL380 (GEN8 OR GEN9); 5 13: SERVER A DL360 (GEN8 OR GEN9) |  |  |  |  | 36 | SERVER A DL380 (GEN8 OR GEN9) |  |  |  | SERVER A DL360 (GEN8 OR GEN9)
|  | 5 4: 35; 5 13: SERVER B DL360 (GEN8 OR GEN9) |  |  |  |  | 35 |  |  |  |  | SERVER B DL360 (GEN8 OR GEN9)
|  | 5 4: 34; 5 9: SERVER B DL380 (GEN8 OR GEN9); 5 13: SERVER C DL360 (GEN8 OR GEN9) |  |  |  |  | 34 | SERVER B DL380 (GEN8 OR GEN9) |  |  |  | SERVER C DL360 (GEN8 OR GEN9)
|  | 5 4: 33; 5 13: SERVER D DL360 (GEN8 OR GEN9) |  |  |  |  | 33 |  |  |  |  | FILLER PANEL
|  | 5 4: 32; 5 9: SERVER C DL380 (GEN8 OR GEN9); 5 13: SERVER E DL360 (GEN8 OR GEN9) |  |  |  |  | 32 | SERVER C DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL
|  | 5 4: 31; 5 13: SERVER F DL360 (GEN8 OR GEN9) |  |  |  |  | 31 |  |  |  |  | FILLER PANEL
|  | 5 4: 30; 5 9: SERVER D DL380 (GEN8 OR GEN9); 5 13: SERVER G DL360 (GEN8 OR GEN9) |  |  |  |  | 30 | FILLER PANEL
|  | 5 4: 29; 5 13: SERVER H DL360 (GEN8 OR GEN9) |  |  |  |  | 29 | FILLER PANEL
|  | 5 4: 28; 5 9: SERVER E DL380 (GEN8 OR GEN9); 5 13: SERVER I DL360 (GEN8 OR GEN9) |  |  |  |  | 28 | FILLER PANEL
|  | 5 4: 27; 5 13: SERVER J DL360 (GEN8 OR GEN9) |  |  |  |  | 27 | FILLER PANEL
|  | 5 4: 26; 5 9: SERVER F DL380 (GEN8 OR GEN9); 5 13: SERVER K DL360 (GEN8 OR GEN9) |  |  |  |  | 26 | FILLER PANEL
|  | 5 4: 25; 5 13: SERVER L DL360 (GEN8 OR GEN9) |  |  |  |  | 25 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace
|  | 5 4: 24; 5 9: SERVER G DL380 (GEN8 OR GEN9); 5 13: FILLER PANEL |  |  |  |  | 24 | (cxen2-bay1) BLADE | (cxen2-bay2) BLADE | (cxen2-bay3) BLADE | (cxen2-bay4) BLADE | (cxen2-bay5) BLADE | (cxen2-bay6) BLADE | (cxen2-bay7) BLADE | (cxen2-bay8) BLADE
|  | 5 4: 23; 5 13: FILLER PANEL |  |  |  |  | 23
|  | 5 4: 22; 5 9: SERVER H DL380 (GEN8 OR GEN9); 5 13: FILLER PANEL |  |  |  |  | 22
|  | 5 4: 21; 5 13: FILLER PANEL |  |  |  |  | 21
|  | 20 | SERVER I DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 20 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 19 |  |  |  |  | FILLER PANEL | [7 empty] | 19 | (cxen2-bay9) BLADE | (cxen2-bay10) BLADE | (cxen2-bay11) BLADE | (cxen2-bay12) BLADE | (cxen2-bay13) BLADE | (cxen2-bay14) BLADE | (cxen2-bay15) BLADE | (cxen2-bay16) BLADE
|  | 18 | SERVER J DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 21 20: 18
|  | 17 |  |  |  |  | FILLER PANEL | [7 empty] | 21 20: 17
|  | 16 | SERVER K DL380 (GEN8 OR GEN9) |  |  |  | FILLER PANEL | [7 empty] | 21 20: 16
|  | 15 |  |  |  |  | FILLER PANEL | [7 empty] | 15 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 14 | SEISMIC BRACE 805-0188-GXX | [8 empty] | Seismic Brace |  |  | 16 15: 14; 16 9: SEISMIC BRACE 805-0188-GXX |  | Seismic Brace
|  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE |  |  |  |  | 13 | (cxen1-bay1) BLADE | (cxen1-bay2) BLADE | (cxen1-bay3) BLADE | (cxen1-bay4) BLADE | (cxen1-bay5) BLADE | (cxen1-bay6) BLADE | (cxen1-bay7) BLADE | (cxen1-bay8) BLADE
|  | 12 | [12 empty] | 16 15: 12
|  | 11 | [12 empty] | 16 15: 11
|  | 10 | [12 empty] | 16 15: 10
|  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  |  | 9 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE |  |  |  |  | 8 | (cxen1-bay9) BLADE | (cxen1-bay10) BLADE | (cxen1-bay11) BLADE | (cxen1-bay12) BLADE | (cxen1-bay13) BLADE | (cxen1-bay14) BLADE | (cxen1-bay15) BLADE | (cxen1-bay16) BLADE
|  | 10 9: 7 |  |  |  |  | 7
|  | 10 9: 6 |  |  |  |  | 6
|  | 10 9: 5 |  |  |  |  | 5
|  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  |  |  |  | 4 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 5 4: 3; 5 9: FILLER PANEL |  |  |  |  | 3 | FILLER PANEL
|  | 5 4: 2; 5 9: FILLER PANEL |  |  |  |  | 2 | FILLER PANEL
|  | 5 4: 1; 5 9: FILLER PANEL |  |  |  |  | 1 | FILLER PANEL
| FRONT VIEW 805-0562-01 WRIGHT LINE CABINET (40U) | [12 empty] | FRONT VIEW 805-0562-01 WRIGHT LINE CABINET (40U)
NOTE 1: THE 870-3103-01 ASSEMBLY SHOWN ABOVE IN FIGURES 1T, 1W, 1X AND 1Y IS THE EAGLE XG PLATFORM SYSTEM IN THE WRIGHT LINE CABINET SUPPORTING BOTH 40U AND 44U TALL CABINETS (SHOWN FOR REFERENCE ONLY SEE ASSEMBLY NOTE 32) WITH GEN9 AND GEN8 SERVERS AND BLADES. THE GEN8 AND GEN9 SERVERS CAN BE MIXED IN THE SAME CABINET. THE SERVERS SHOWN ABOVE IN FIGURE 1T, 1W, 1X AND 1Y COULD BE DL380 GEN8 SERVERS OR THE HP DL380 GEN9 SERVER. BOTH SERVERS ARE 2U SERVER SO THERE IS NO RESTRICTIONS FOR INSTALLING A HP DL380 GEN9 SERVER IN ANY AVAILABLE SERVER POSITION. ALL SERVERS ARE FRONT MOUNTED AND THE 4948E-F SWITCHES WILL BE REAR MOUNTED. PDUS ARE MOUNTED IN THE REAR WITH ACCESS FROM THE REAR OF THE CABINET. INSTALL THE PANDUIT AIR DUCT FOR SWITCH "A" IN U39-U40 AND THE AIR DUCT FOR SWITCH B IN U41-U42. AIR DUCT IS 2U HIGH AND THE AIR INTAKE GRILL SHOULD BE MOUNTED IN THE FRONT OF THE CABINET. THE SWITCHES WILL MOUNT IN THE AIR DUCT WITH THE ETHERNET PORTS FACING THE REAR OF THE CABINET, SEE PANDUIT ASSEMBLY INSTRUCTIONS AND FIGURES 2 AND 3. FILLER PANELS IN ALL OPEN U LOCATIONS.
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure.
NETWORK ZONE (U41-U44)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
NETWORK ZONE (U37-U40)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
Zone 2 (U15-U25)
2nd c7000 enclosure (cxen2) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure.
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure.
Zone 2 (U15-U25)
2nd c7000 enclosure (cxen2) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure.
Zone 3 (U26-U36)
3 x 1U serves HP DL380 GEN8 OR GEN9 servers or 3 x 2U servers HP DL380 GEN8 OR GEN9 servers if 2nd c7000 enclosure (cxen2) is installed. Install filler panels if open in front of cabinet.
NETWORK ZONE (U41-U44)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) 805-0592-02
(Mount switch in the Panduit Air Duct PN 805-0593-01)
Zone 3 (U26-U40)
15U Reserved for Server A through Server C
3 HP DL360 GEN8 OR GEN9 servers or 3 HP DL380 GEN8 OR GEN9 servers if 2nd c7000 enclosure (cxen2) is installed. Existing systems hace filler panels in all open in front of cabinet
Zone 2 (U15-U25)
2nd c7000 enclosure (cxen2) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
NETWORK ZONE (U37-U40)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) 805-0592-02
(Mount switch in the Panduit Air Duct PN 805-0593-01)
Zone 3 (U26-U36)
3 DL360 servers or 3 DL380 servers or a mix of server types if 2nd c7000 enclosure (cxen2) is installed. Install filler panels if open in front of cabinet
Zone 2 (U15-U25)
2nd c7000 enclosure (cxen2) 805-0540-GXX
See Figure 1E and Assy Note 25 for guidelines on Blade placement in c7000 enclosure
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure.
Zone 2 and Zone 3 (U15-U36)
12 x 1U servers HP DL360 GEN8 OR GEN9 servers or 11 x 2U serves HP DL380 GEN8 OR GEN9 servers is supported if the 2nd c7000 enclosure (cxen2) is not installed. Install filler panels if open in front of cabinet.
Zone 2 and Zone 3 (U15-U40)
12 x 1U servers HP DL360 GEN8 OR GEN9 servers or 12 x 2U servers HP DL380 GEN8 OR GEN9 servers if the 2nd c7000 enclosure (cxen2) is not installed. Install filler panels if open in front of cabinet.
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
Zone 2 and Zone 3 (U15-U40)
12 DL360 GEN8 OR GEN9 servers or 11 DL380 GEN8 OR GEN9 servers if the 2nd c7000 enclosure (cxen2) is not installed. Install filler panels if open in front of cabinet.
NETWORK ZONE (U37-U40)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
Zone 2 and 3 (U15-U36)
12 DL360 GEN8 OR GEN9 servers or 11 DL380 GEN8 OR GEN9 servers if the 2nd c7000 enclosure (cxen2) is not installed. Install filler panels if open in front of cabinet.
Zone 1 (U4-U14)
1st c7000 enclosure (cxen1) 805-0540-GXX
See Assy Note 25 for guidelines on Blade placement in c7000 enclosure
NETWORK ZONE (U37-U40)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted) PN 805-0592-02
(Mount switch in the Panduit Air Duct) PN 805-0593-01
NETWORK ZONE (U41-U44)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted)
PN 805-0592-02
(Mount switch in the Panduit Air Duct
PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted)
PN 805-0592-02
(Mount switch in the Panduit Air Duct
PN 805-0593-01)
Zone 3 (U26-U40)
3 x 1U servers HP DL360 GEN8 OR GEN9 servers or 3 x 2U servers HP DL380 GEN8 OR GEN9 servers if 2nd c7000 enclosure (cxen2) is installed. Install filler panels if open in front of cabinet
NETWORK ZONE (U37-U40)
4U Reserved for Switches
● SWITCH B (Top switch, rear mounted)
PN 805-0592-02
(Mount switch in the Panduit Air Duct
PN 805-0593-01
● SWITCH A (Bottom switch, rear mounted)
PN 805-0592-02
(Mount switch in the Panduit Air Duct
PN 805-0593-01)
870-3103-01_WL_GEN8_GEN9_Cabinet Layout
Install filler panels in all open spaces as shown
the existing Wright Line cabinet will have all open "U" locations filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
the existing Wright Line cabinet will have all open "U" locations filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
the existing Wright Line cabinet will have all open "U" locations filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
the existing Wright Line cabinet will have all open "U" locations filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
the existing Wright Line cabinet will have all open "U" locations filled with a filler panel. See 870-3103-01 picklist for filler panel part number.
Install filler panels in all open spaces as shown
the existing Wright Line cabinet will have all open "U" locations filled with a filler panel. See 870-3103-01 picklist for filler panel part number.

## Assembly Notes
ASSEMBLY NOTES:
1. THE DETAILS AND FIGURES IN THIS DOCUMENT REPRESENT THE HP CABINET AND ASSOCIATED HARDWARE FROM HP AND OTHERS. IF THE CABINET IS BUILT BY ORACLE SERVICES THE FIGURES AND ASSOCIATED DETAILS IN THIS DOCUMENT WILL SUPPORT BUILDING THE HW COMPONENT OF A SYSTEM IN A HP CABINET USING ORACLE RELEASED HARDWARE, CABLES AND LABELS. THE END USER MAY ORDER THE CABINET FROM ORACLE OR THEY MAY PURCHASE ANY MANUFACTURERS CABINET (CABINET MUST MEET EIA-310 D Type A per section 4.1.1.) AND ASSOCIATED HARDWARE. THE END USER IS REQUIRED TO ORDER THE SERVERS AND OTHER COMPONENTS AS REQUIRED TO BUILD THE HW COMPONENT OF THE SYSTEM. THE SERVER CONFIGURATIONS ARE SHOWN IN APPENDIX A. THIS ASSEMBLY IF BUILT BY ORACLE SERVICES OR BUILT BY THE END USER MUST CONFORM TO THIS DOCUMENT WITH NO ADDITIONS, DELETIONS, SUBSTITUTIONS, OR MODIFICATIONS ON THE CABINET ASSEMBLY AND SERVER CONFIGURATIONS WITHOUT PRIOR WRITTEN ORACLE APPROVAL.
2. SHIPMENT OF A CONFIGURED RACK (WITH MOUNTED COMPONENTS) MUST BE DONE IN ACCORDANCE WITH HP DOCUMENTATION. FOR THE 805-0614-XX HP CABINET USE, "HP Intelligent Rack Family User Guide".
3. TORQUE ALL FASTENERS IN ACCORDANCE WITH MANUFACTURER SPECIFICATIONS. C7000 INPUT CONNECTIONS SHOULD BE TORQUED TO 36 IN-LB PER HP RECOMMENDATIONS.
4. RACK IS SUPPLIED ON A SHIPPING PALLET. ALL SHIPPING MATERIAL MUST BE RETAINED INCLUDING THE PALLET FOR FINAL SHIPMENT TO FINAL CUSTOMER DESTINATION IF BUILD IS BEING STAGED IN ANOTHER FACILITY. SEE FIGURE 45 FOR PRE SHIPPING INSTRUCTIONS.
5. THE RACK ACCESSORIES: STABILIZER KIT AND TIE DOWN KIT ARE TO BE SHIPPED WITH RACK. THESE ACCESSORIES ARE TO BE INSTALLED IN THE FIELD.
6. INSTALL OPTIONAL COMPONENTS AS REQUIRED. THIS IS A CONFIGURABLE SYSTEM AND THE ORDER WILL SPECIFY THE PART NUMBERS AND QUANTITIES. LOCATING DIMENSIONS FOR ALL SERVERS, POWER AND NETWORK ACCESS COMPONENTS ARE SHOWN BY RACK "U" AND ARE SHOWN ON THE CABINET LAYOUT TAB FOR THE MAXIMUM CONFIGURED CABINET. SEE SYSTEM INTERCONNECT DRAWING 892-0125-01 FOR ADDITIONAL DETAILS AND PART NUMBERS. SEE FIGURE 1A THROUGH 1L FOR CABINET LAYOUTS.
7. THE PDU'S SHOWN IN FIGURE 1A THROUGH 1L ARE HP STANDARD POWER PANELS, SEE PICK LIST FOR HP PN. ALL MOUNTING HARDWARE FOR THE PDUS ARE SUPPLIED WITH THE HP PDUS AND HP CABINET. THE HP PDUS ARE INSTALLED IN THE FRONT OF THE CABINET STARTING AT THE 1U LOCATION. SEE POWER TABLES B-J AND 892-0125-01 FOR ADDITIONAL DETAILS AND PART NUMBERS. IF USING THE HP POWER PANELS USE THE FOLLOWING GUIDELINES: • SINGLE PHASE POWER PANELS ( MAX 6 HP PDU UNITS PER CABINET): a) PDU A1 AND B1 SUPPLY POWER TO THE FIRST C7000 ENCLOSURE (EN1), AS WELL AS THE A1-X AND B1-X EXTENSION BARS. b) PDU A2 AND B2 SUPPLY POWER TO THE SECOND ENCLOSURE (EN2). c) PDU A3 AND B3 SUPPLY POWER TO THE THIRD ENCLOSURE (EN3) OR CO-MINGLED RACKMOUNT SERVERS. • THREE PHASE POWER PANELS (FOUR HP PDUS MAX): a) PDU A1 AND B1 SUPPLY POWER TO THE FIRST C7000 ENCLOSURE (EN1), TWO OF THE POWER SUPPLIES OF THE THIRD ENCLOSURE (EN3), AS WELL AS THE A1-X AND B1-X EXTENSION BARS. b) PDU A2 AND B2 SUPPLY POWER TO THE SECOND ENCLOSURE (EN2) AND FOUR POWER SUPPLIES OF THE THIRD ENCLOSURE (EN3).
8. THE ENCLOSURE SWITCHES MAY BE PROCURVE 6120XG, HP6125G, HP6125XLG OR PASS-THRU MODULES. POPULATE THE C7000 I/O BAYS IN THE FOLLOWING ORDER: a. PROCURVE 6120XG OR HP6125XLG FROM I/O BAY 1-8 DEPENDING ON THE NUMBER OF SWITCHES ON THE ORDER b. HP6125G FROM I/O BAY 1-8 DEPENDING ON REMAINING OPEN BAYS c. PASS-THRU MODULES FROM I/O BAYS 5-8 DEPENDING ON REMAINING OPEN BAYS
THE PICK LIST CONTAINS A LIST OF THE SFP MODULES FOR THE DIFFERENT SWITCH TYPES AND CABLE TYPES THAT ARE SUPPORTED. (SEE TR007055 FOR MORE DETAIL ON SWITCH SFP COMBINATIONS)
9. THE CISCO 4948E-F SWITCHES MAY BE SUPPLIED BY THE CUSTOMER OR ORDERED FROM ORACLE. THE 4948E-F REQUIRES THE PANDUIT AIR DUCT TO DIRECT AIR AND TO SUPPORT THE SWITCH. NO ADDITIONAL SUPPORT BRACKETS WILL BE REQUIRED. LOCATE THE AIR DUCT FOR THE SWITCHES AS SHOWN IN FIGURE 1A-1L. MOUNT THE AIR DUCT PER PANDUIT INSTALLATION INSTRUCTIONS (SEE FIGURE 3 AND 4). THE POWER CORDS SUPPLIED WITH THE SWITCH ARE C13 TO NEMA 5-15P. THE POWER CORD TO CONNECT TO THE HP PDU REQUIRES C13 TO C14 AC POWER CABLE AND TWO POWER CABLES PER SWITCH AND ARE INCLUDED IN THE 7306951 KIT, THE CUSTOMER WILL BE RESPONSIBLE TO PROVIDE THE POWER CORDS IF USING A DIFFERENT MANUFACTURER PDU. THE PLASTIC CABLE GUIDE SUPPLIED WITH THE SWITCH IS NOT REQUIRED IF THE 7306951 KIT IS ORDERED. THE PANDUIT AIR DUCT IS SUPPLIED WITH MOUNTING HARDWARE FOR THE SQUARE HOLE (SEE FIGURE 2 FOR THE DIFFERENT TYPES OF CABINET MOUNTING RAILS AND THE HARDWARE THAT MAY BE REQUIRED TO MOUNT THE PANDUIT AIR DUCT WITH SWITCHES IN THE CABINET).
10. THE HP HARDWARE WILL BE SUPPLIED BY THE CUSTOMER. THE SUPPORTED HP DL380 GEN9 SERVER CONFIGURATIONS MAY BE VIEWED IN APPENDIX A. ALL CONFIGURED SERVERS FROM HP SHIP WITH A STANDARD SIX FOOT IEC C-13/C-14 JUMPER CORD (A0K02A).THIS JUMPER CORD IS ALSO INCLUDED WITH EACH STANDARD AC POWER SUPPLY OPTION KIT. THE HP C7000 ENCLOSURE IS BUILT WITH THE C7000 - 2400W PLATINUM POWER SUPPLY BUNDLE FROM HP, THE ENCLOSURE HAS QTY 6 POWER SUPPLIES AND THE C7000 ENCLOSURE COMES WITH (QTY 6) SIX FOOT IEC C19-C20 CORDS IF A DIFFERENT CORD IS REQUIRED, PLEASE CHECK THE HP C7000 QUICK SPEC FOR POWER CABLE OPTIONS. THE POWER CORDS THAT ARE SUPPLIED WITH THE SERVERS AND C7000 ENCLOSURES ALSO WORK WITH THE HP PDU'S. THE HP SERVER HARDWARE KIT SUPPORTS INSTALLING IN A RACK WITH SQUARE HOLES AND THE ENCLOSURE HARDWARE KIT FROM HP COMES WITH (QTY 4) CAGE NUTS FOR SQUARE HOLE RACKS AND (QTY 4) CLIP NUTS FOR ROUND HOLE RACKS.
11. INSTALL FILLER PANELS AS REQUIRED TO FILL ALL U LOCATIONS IN THE FRONT OF THE RACK TO MAINTAIN PROPER COOLING (SEE FIGURES 1A THROUGH 1L). NO FILLER PANELS ARE REQUIRED IN REAR OF THE CABINET. BLADE FILLER PANELS SHALL BE USED IN ALL OPEN BLADE BAYS OF THE ENCLOSURE (FRONT AND REAR).
12. FOR SERVER "A" SERIAL INTERFACE TO THE SWITCHES: SEE CABLE TABLES AND SYSTEM INTERCONNECT FOR MORE INFORMATION. A) HP DL380 GEN8 SERVER: IF SWITCHES ARE PRESENT IN THE SYSTEM WITH GEN8 DL380 SERVERS THEN THE SERIAL INTERFACE FROM SERVER A TO THE SWITCHES SHOULD ALREADY BE INSTALLED. B) HP DL380 OR DL360 GEN9 SERVER: THE SERIAL INTERFACE FROM SERVER A TO THE SWITCHES USES THE USB TO 9 PIN ADAPTER CABLE (PN 804-2966-G01) AND WILL USE THE TWO USB PORTS ON THE REAR OF THE SERVER (USB0 AND USB1). ATTACH THE USB TO 9 PIN ADAPTER CABLE AS SHOWN ON SYSTEM INTERCONNECT BETWEEN SERVER A AND SWITCHES A AND B. SECURE THE SERIAL CABLE TO PREVENT DAMAGE. ALL OTHER SERVERS (SERVER B THROUGH SERVER L) WILL NOT REQUIRE THE USB TO 9 PIN ADAPTER CABLE.
13. LABEL ALL POWER AND DATA CABLES. THE POWER TABLES ARE SHOWN ON THE AC POWER TABLES TABS. THE POWER TABLES IN THIS DOCUMENT REPRESENT USING THE HP PDU'S. NO DATA CABLE TABLES ARE INCLUDED IN THIS DOCUMENT. THE NETWORKING IS CUSTOMER SPECIFIC AND THE TOPOLOGY TR 821-0068-01 AND SYSTEM TOPOLOGY INTERCONNECT 892-0123-01 WILL DEFINE THE SYSTEM ETHERNET AND SERIAL CONNECTIONS. THE HP POWER CABLE TABLES IN THIS DOCUMENT WILL SHOW THE CABLE PART NUMBER AND THE "FROM/TO" TEXT WHEN USING THE HP POWER UNITS (PDU's). THE LABEL TEXT LAYOUT AND LABEL LOCATION IS SHOWN IN FIGURE 23. THE LABEL TEXT SIZE SHALL BE .06-.12 HIGH, COLOR TO BE BLACK OR APPROVED EQUIVALENT. USE CABLE LABEL PN 617-0009-01 OR APPROVED EQUIVALENT TO LABEL ALL CABLES. LOCATE THE CABLE LABEL WITH THE FROM/TO INFORMATION PRINTED ON THE LABEL AS FOLLOWS, ONE LABEL AT EACH END OF THE CABLE AS SHOWN IN FIGURE 23. THE CABLE LABEL LOCATION SHOULD NOT OVERLAP THE MANUFACTURERS PART NUMBER LABEL AND BE WITHIN 1.00+/-.50 FROM THE MANUFACTURERS PART NUMBER LABEL OR WITHIN 6" OF THE CABLE CONNECTOR. LABEL SHOULD NOT INTERFERE WITH BEND RADIUS, ALLOWANCES SHALL BE MADE TO ACCOMMODATE CABLE ROUTING.
14. GROMMET MATERIAL PN 616-0730-G01 (PART OF THE 870-3111-01 ) SHALL BE USED, AS REQUIRED, TO PROTECT THE CABLES AND WIRES FROM ANY SHARP EDGES WHEN ROUTING THE CABLES IN THE CABINET.
15. IF THE ORDER INCLUDES HP PDU 804-2062-G07, USE LABEL 903-0122-01 OR EQUIVALENT TO PRINT "40 AMPS PER PDU". IF ORDER INCLUDES HP PDU 804-2062-G10, USE LABEL 903-0122-01 OR EQUIVALENT TO PRINT "69AMPS PER PDU". APPLY THIS LABEL OVER THE EXISTING TEXT "30 A PER PDU" ON CONSOLIDATED SYSTEM LABEL 658-0770-11, AS SHOWN. SEE FIGURE 25 FOR ADDITIONAL LABELING DETAILS.
16. POWER AND DATA CABLES SHALL NOT BE ROUTED IN PARALLEL WITHIN 1 INCH OF EACH OTHER. THESE CABLES CAN CROSS EACH OTHER BUT NOT BE TIED TOGETHER.
17. LABEL THE HP PDU AND EXTENSION BAR CABLES NEAR THE PLUG END OF THE CABLE.
18. THE ENCLOSURE SWITCHES ARE LINE ITEMS ON THE ORDER. ENCLOSURE SWITCHES ARE TO BE INSTALLED PER ASSEMBLY NOTE 8.
19. AN EXTENSION CABINET CONSISTS OF A CABINET WITHOUT AGGREGATION SWITCHES OR MANAGEMENT SERVER. THIS EXTENSION CABINET IS CONNECTED TO THE SWITCHES IN THE FIRST CABINET AS SHOWN IN THE SPECIFIC NETWORK TOPOLOGY FOR THAT IMPLEMENTATION PER REFERENCES 11 AND 12.
20. IF THE CABINET HAS RACKMOUNT SERVERS IN A CO-MINGLED CONFIGURATION, THE PDUS WILL HAVE EXTENSION BARS CONNECTED AND MOUNTED IN THE CABINET AS SHOWN IN THE CABINET LAYOUTS, FIGURES 1A-1L. POWER CABLE CONNECTIONS ARE SHOWN IN TABLES B-E AND REFERENCE 16 TO SUPPORT THE HP PDU PANELS.
21. THE SYSTEMS BUILT IN MORRISVILLE WILL USING THE ASSEMBLY MATERIALS KITS TO ASSEMBLE THE CABINET. THE EXTRA HARDWARE SHOULD SHIP WITH THE CABINET.
22. THE ASSEMBLY INSTALLATION KITS ARE DESIGNED TO CONTAIN ALL THE HARDWARE NEEDED FOR INSTALLATION OF THE HARDWARE COMPONENT.
23. CABLES SHALL BE ROUTED SUCH THAT THE BEND RADIUS MEETS ORACLE MANUFACTURING STANDARDS. CABLE TIES SHOULD BE CUT FLUSH AND TURNED TOWARDS THE INSIDE OF THE CABINET.
24. GROMMET MATERIAL PN 616-0730-G01 TO BE USED, AS REQUIRED, TO PROTECT THE CABLES AND WIRES FROM ANY SHARP EDGES WHEN ROUTING THE CABLES IN THE CABINET.
25. BLADES ARE INSTALLED IN THE FOLLOWING ORDER:
a. FULL HEIGHT BLADES FROM LEFT TO RIGHT STARTING WITH BAY 1/9
b. DIH PROCESSING BLADE IN BAY 15 AND STORAGE BLADE IN BAY 16. ANY ADDITIONAL STORAGE ASSEMBLIES CAN BE INSTALLED IN ANY ODD/EVEN BAY COMBINATION. STORAGE BLADE NEEDS TO BE INSTALLED NEXT TO AND TO THE RIGHT OF ITS PROCESSING BLADE.
c MANAGEMENT BLADE IN BAY 8 (OAM/CMP).
d. SECOND MANAGEMENT BLADE IN BAY 7 (IF APPLICABLE)
e. FILL THE REMAINDER OF THE HALF HEIGHT SLOTS STARTING WITH BAY 1 AND CONTINUING IN ANY OPEN BAY SEQUENTIALLY. INSTALL THE BLADES IN ORDER NUMERICALLY.
f. IF THERE IS MORE THAN ONE ENCLOSURE ON AN ORDER, THE BLADES SHOULD BE SPLIT EVENLY BETWEEN THE ENCLOSURES AND INSTALLED FOLLOWING THE ABOVE RULES.
26. NETWORKING FOR THE CABINET CONFIGURATION SHALL BE DONE IN ACCORDANCE WITH THE TOPOLOGIES LISTED ON THE TOPOLOGY TABLES IN TR 821-0068-01 AND 892-0123-01 TOPOLOGY SYSTEM INTERCONNECT. REFER TO THE WORK ORDER OR HOW THE SYSTEM WILL BE INTEGRATED INTO THE NETWORK TO DETERMINE THE SPECIFIC TOPOLOGY FOR THE CABINET CONFIGURATION.
27. MASTER LABEL PN 7300465 SUPPORTS LABELING THE HARDWARE USED TO BUILD THE EAGLE XG CABINET. LABEL FRONT AND REAR OF CABINET USING LABEL PN 7300465 OR APPROVED EQUIVALENT. APPLY THE SERVER POSITION LABELS AS SHOWN IN FIGURES 27, 28 AND 29 FOR THE HP SERVERS. LABEL THE 4948E-F SWITCHES AS SHOWN IN FIGURE 30 AND 31. LABEL THE PDU AND EXTENSION BARS AS SHOWN IN FIGURES 20, 21 AND 22. APPLY LABEL TO THE CABINET DOOR AS SHOWN IN FIGURE 24.
28. IF THE CABINET HAS 2U SERVERS AND DL360 RACKMOUNT SERVERS IN A CO-MINGLED CONFIGURATION, THE 2U SERVERS SHOULD BE INSTALLED FIRST AND THE DL360 SERVERS INSTALLED NEXT.
ASSEMBLY NOTES TAB

## 870-3111-01_Cab Assy_Details
870-3111-01_Cab Assy_Detail
FIGURE 2: Cabinet Mounting Rails and Mounting Hardware
(ASSEMBLY NOTE 10)
Round-hole racks
Square-hole racks
Threaded-hole racks
FIGURE 3: Panduit Air Duct and CISCO 4948E-F SWITCH MOUNTED VIEW
(ASSEMBLY NOTE 9)
FIGURE 4: Panduit Air Duct and CISCO 4948E-F Switch Mounting Detail
(ASSEMBLY NOTE 9)
FIGURE 5: HP C7000 ENCLOSURE GEN9 CABINET ASSY VIEWS SHOWN INSTALLED IN HP CABINET
ENCLOSURE I/O BAY 2
THE FOLLOWING ITEMS ARE STANDARD FOR THE HP CABINET AND SHOULD BE INSTALLED PER THE MANUFACTURERS SUPPLIED INSTALLATION INSTRUCTIONS OR AS INDICATED:
● HP BW904A_642 1075MM_SHOCK INTELLIGENT SERIES RACK_ROHS
●HP BW926A_600MM_RACK TIE DOWN KIT (DO NOT INSTALL TO BE SHIPPED LOOSE AND INSTALLED IN THE FIELD)
●HP BW906A_42U 1075MM_SIDE PANEL KIT (INSTALL PRIOR TO SHIPPING)
●HP BW932A_600MM_JB_RACK STABILIZER KIT (DO NOT INSTALL TO BE SHIPPED LOOSE AND INSTALLED IN THE FIELD)
●HP BW891A_GROUNDING KIT (INSTALL ALL GROUND STRAPS PER INSTRUCTIONS PROVIDED BY MANUFACTURE)
●HP BW929A (pack of 100) INSTALL FILLER PANELS ( PN 804-2085-G01) AS REQUIRED TO FILL ALL FRONT PANEL SPACES
SEE TR007457 FOR SERVER AND BLADE CONFIGURATIONS.
See Assembly Notes.
FRONT DOOR
FRONT VIEW
REAR VIEW
REAR DOOR
INSTALL THE PANDUIT AIR DUCT PER THE MANUFACTURERS INSTRUCTIONS USING THE HARDWARE SUPPLIED WITH THE AIR DUCT KIT (TYP BOTH SIDES). IF THE ASSEMBLY MATERIALS KIT IS PURCHASED 814-0033-02 OR ON THE ORDER THEN INSTALL THE CABLE MANAGEMENT BARS FOR EACH SWITCH BY SECURING THE BAR USING THE LOWER MOUNTING HOLE ON THE AIR DUCT TO SECURE THE BAR TO THE CABINET USING HARDWARE SUPPLIED WITH AIR DUCT. NOTE ORIENTATION OF CABLE MANAGEMENT BAR INSTALL AS SHOWN.
USE THE FOUR (4) ACORN NUTS (#10-32) SUPPLIED WITH AIR DUCT TO INSTALL THE SWITCH AS SHOWN. MOUNTING HARDWARE IS SUPPLIED WITH THE PANDUIT AIR DUCT TO INSTALL AIR DUCT. (TYPICAL EACH SWITCH) (TYP BOTH SIDES)
PANDUIT AIR DUCT
SWITCH B (4948E-F)
(NOT SHOWN) BOTTOM OF PANDUIT AIR DUCT SHOWN FOR REFERENCE ONLY
SWITCH A (4948E-F)
INSTALL THE PANDUIT AIR DUCT PER THE MANUFACTURERS INSTRUCTIONS. MOUNTING HARDWARE IS INCLUDED TO MOUNT THE AIR DUCT TO THE CABINET FRONT AND REAR CABINET RAILS
REAR VIEW
FRONT VIEW
ENTERPRISE 42U AC CABINET
3-C7000 ENCLOSURES, 1-DL380 GEN9 SERVER AND 2-4948E-F SWITCHES
FOR CABINETS WITH ROUND HOLE MOUNTING RAILS THE CUSTOMER WILL BE RESPONSIBLE FOR PROVIDING THE MOUNTING HARDWARE TO MOUNT THE HARDWARE IN THE CABINET. THE HP SERVER REQUIRES A 5MM CLIP NUT AND THE PANDUIT AIR DUCT REQUIRES A 12-24 CLIP NUT. THE HP ENCLOSURE REQUIRES A 6MM CLIP NUT (SUPPLIED WITH ENCLOSURE). MOUNT ALL HARDWARE PER MANUFACTURERS INSTRUCTIONS.
FOR CABINETS WITH SQUARE HOLE MOUNTING RAILS THE CUSTOMER WILL BE RESPONSIBLE FOR PROVIDING THE MOUNTING HARDWARE. THE HP SERVERS, ENCLOSURES AND PANDUIT AIR DUCT ARE SUPPLIED WITH HARDWARE TO MOUNT IN A 3/8"SQ HOLE, NO MOUNTING HARDWARE IS REQUIRED IF THE OPENING IN THE MOUNTING RAILS ACCEPTS A 3/8" U NUT TYPE FASTENER. MOUNT ALL HARDWARE PER MANUFACTURERS INSTRUCTIONS.
FOR CABINETS WITH THREADED HOLE MOUNTING RAILS THE CUSTOMER WILL BE RESPONSIBLE FOR THE MOUNTING HARDWARE TO MOUNT THE HP SERVERS, ENCLOSURES AND THE PANDUIT AIR DUCT. MOUNT ALL HARDWARE PER MANUFACTURERS INSTRUCTIONS.

## 870-3103-01_Cab_Assy_Details
FIGURE 10: Panduit Air Duct (CDE2) and CISCO 4948E-F SWITCH
(ASSEMBLY NOTE 9)
FIGURE 11: Panduit Air Duct and CISCO 4948E-F SWITCH MOUNTING DETAIL
(ASSEMBLY NOTE 9)
FIGURE 12: TYPICAL CAGE NUT INSTALLATION DETAIL IN A CABINET WITH SQUARE HOLES
(ASSEMBLY NOTE 10)(NOTE RACK U SHOWN FOR REFERENCE ONLY ACTUAL LOCATION MAY NOT USE RACK U SHOWN)
FIGURE 13: TYPICAL MOUNTING DETAIL DL380 GEN9 SERVER IN A CABINET WITH SQUARE HOLES
FIGURE 14: INSTALLING A c7000 ENCLOSURE INTO A WRIGHT LINE CABINET
Step 1) Unpack the c7000 enclosure and discard the mounting rail that comes with the enclosure.
Step 2) Locate the mounting rail within the Seismic Kit 805-0188-G01 and install with the included hardware as shown here.
INSTALL THE CAGE NUTS THAT COME WITH THE CABINET AS REQUIRED. CAGE NUT AND SCREW KIT PN 804-1656-01 WRIGHT LINE JHBLKCG1032_10-32 CAGE NUT AND 10-32 X .625 LONG BLACK SCREW_KIT_ROHS
MOUNT DL380 SERVER USING HARDWARE SHOWN (SUPPLIED WITH SERVER) INSTALL ONE 5MM CAGE NUT FRONT SURFACE AND ONE CAGE NUT REAR SIDE TO ALIGN WITH THE SECOND HOLE ON THE SERVER RAILS (TYPICAL BOTH SIDES)
MOUNT DL380 SERVER USING HARDWARE SHOWN (SUPPLIED WITH SERVER) INSTALL ONE 5MM SCREW FRONT SURFACE AND ONE CAGE NUT REAR SIDE TO ALIGN WITH THE SECOND HOLE ON THE SERVER RAILS (TYPICAL BOTH SIDES)
PRIOR TO SHIPPING TIGHTEN CAPTIVE SCREW IN HANDLE TO SECURE SERVER DURING SHIPPING (TYPICAL BOTH SIDES)
INSTALL THE SEISMIC RAIL FOR THE C7000 USING THESE INCLUDED SCREWS IN THE U4 LOCATION. THE SECOND C7000 AND SET OR RAILS IS INSTALLED IN THE U15 LOCATION.
870-3103-01_Cab_Assy_Details Tab
INSTALL THE PANDUIT AIR DUCT PN 805-0593-01 PER THE MANUFACTURERS INSTRUCTIONS USING THE HARDWARE SUPPLIED WITH THE AIR DUCT (TYP BOTH SIDES). INSTALL THE CABLE MANAGEMENT BARS FOR EACH SWITCH BY SECURING THE BAR USING THE LOWER MOUNTING HOLE ON THE AIR DUCT TO SECURE THE BAR TO THE CABINET USING HARDWARE SUPPLIED WITH AIR DUCT.
NOTE ORIENTATION OF CABLE MANAGEMENT BAR INSTALL AS SHOWN.
USE THE FOUR (4) ACORN NUTS (#10-32) SUPPLIED WITH AIR DUCT TO INSTALL THE SWITCH AS SHOWN. MOUNTING HARDWARE IS SUPPLIED WITH THE PANDUIT AIR DUCT TO INSTALL AIR DUCT. (TYPICAL EACH SWITCH) (TYP BOTH SIDES)
SWITCH B (4948E-F)
(NOT SHOWN) BOTTOM OF PANDUIT AIR DUCT SHOWN FOR REFERENCE ONLY
SWITCH A (4948E-F)
INSTALL THE PANDUIT AIR DUCT PN 805-0593-01 PER THE MANUFACTURERS INSTRUCTIONS. MOUNTING HARDWARE IS INCLUDED USE THE CAGE NUTS AND SCREWS TO MOUNT THE AIR DUCT TO THE CABINET FRONT AND REAR CABINET RAILS
REAR VIEW
PANDUIT AIR DUCT
FRONT VIEW

## Typical Cable Routing
TYPICAL CABLE ROUTING TAB
FIGURE 10: DATA CABLE ROUTING
(THIS IS AN EXAMPLE OF WHAT THE COMPONENTS AND CABLING MAY LOOK LIKE IN A CABINET. ACTUAL NUMBER OF COMPONENTS WILL BE DETERMINED BY THE SALES ORDER)
CABLES ARE SHOWN IN COLOR FOR CLARITY AND FOR REFERENCE ONLY. COLOR OF CABLE IS DETERMINED BY THE CABLE PART NUMBER.

## 870-3111-01_Component Labeling
870-3111-01_Component Labeling Tab
General Labeling Notes: The following labeling notes WILL ONLY apply if the customer has the Oracle label PN 7300465 to label components. If cabinet is built by Oracle manufacturing the cabinet and cable labeling will be required.
1) Rack Mount Servers position are to be labeled on the front and rear mounting rails as shown in Fig 27 thru Fig 29. This is typical for all servers. (i.e. SERVER A)
2) The Cisco 4948E-F switches are to be labeled on the left hand side mounting rail (front and rear using 7300465. See Figure 30 thru Figure 31.
3) All power and data cables shall be labeled as shown in Figure 23. The "FROM/TO" detail is shown on the POWER AND DATA Cable tabs of this document. There are two labels on each cable. The "TO" portion of the label goes on the end of the cable that is attaching "TO" that destination.
4) Equipment code abbreviations are as follows: ● Cabinet designation - Cx - where x is the cabinet number in the line-up (1-x) ● c7000 enclosure - eny - where y is the enclosure number in the cabinet (1-3) ● Cisco Aggregation switch - agx - where x is the switch number (A/B) ● Server blade - bayx - where x is the bay number of the server (1-16) ● Ethernet blade switch - swx - where x is the I/O bay location (1-8) ● OAx - where x is the number of the Onboard Administrator (OA1 - left from rear; OA2- right from rear) ● SERVER Z - where Z is the letter of the Server (starting with SERVER A)
5) Cable Label Text height shall be .06-.12 high; text in contrasting color to label.
6) PDUS should be labeled on the front face of the PDU module using label PN 7300465 approx sown in Figure 20-22 depending on the type of PDU.
7) Label front door as shown in Figure 24. Label is part of the 870-3111-01 BOM.
8) Consolidated label part of 870-3111-01 BOM. Locate as shown in Figure 25 and apply associated labels as shown in Detail B of Figure 25.
9) Use 7300465 to label all components as required in the cabinet. Use the labels from Column B and C to label the servers and switches. See Figure 26 for label format.
PDU labeling. Use label 7300465. See Cabinet Layout for PDU and Ext. bar location.
Place on the front face of the PDU approximately as shown.
FIGURE 20: SINGLE PHASE PDU LABELING
(SEE GENERAL LABELING NOTE 6)
PDU A1
PDU B1
PDU A2
PDU B2
PDU A3
PDU B3
FIGURE 21: THREE PHASE PDU LABELING
(SEE GENERAL LABELING NOTE 6)
FIGURE 22: EXTENSION BAR LABELING
(SEE GENERAL LABELING NOTE 6)
Place on the front face of the extension bar approximately as shown.
A1-4
B1-4
A3-4
B3-4
A3-3
B3-3
FIGURE 23 : CABLE LABELING
(SEE ASSY NOTE 13 AND GENERAL LABELING NOTE 3)
FIGURE 24 : FRONT DOOR LABELING (PART OF 870-3111-01)
(SEE GENERAL LABELING NOTE 7)
FIGURE 25 : CONSOLIDATED LABEL FOR CABINET (PART OF 870-3111-01 BOM)
(SEE GENERAL LABELING NOTE 8)
FIGURE 26: CABINET LABEL
SEE GENERAL LABELING NOTE 9
FIGURE 27: CABINET LABELING -DL380 GEN9 SERVERS FRONT RAIL
SEE GENERAL LABELING NOTE 1
FIGURE 28: CABINET LABELING -DL360 GEN 9 SERVERS FRONT RAIL
SEE GENERAL LABELING NOTE 1
FIGURE 29: CABINET LABELING -TYPICAL SERVERS LABELING REAR RAIL
SEE GENERAL LABELING NOTE 1
FIGURE 30: CABINET LABELING 4948E-F SWITCHES- FRONT RAIL
SEE GENERAL LABELING NOTE 2
FIGURE 31: CABINET LABELING 4948E-F SWITCHES- REAR RAIL
SEE GENERAL LABELING NOTE 2
LABEL CABLE AS SHOWN IN POWER CABLE TABLES
7300465 Label Set use the labels from Column C to label the switches.
7300465 Label Set use the labels in column "C" for servers and switches.
7300465 Label Set use the labels for servers and switches.
7300465 Label Set use the labels for servers and switches.
7300465 Label Set use the labels for servers and switches.
DETAIL B
POSITION 1
POSITION 7
7300465 LABEL
LABEL CABLE AS SHOWN IN TABLE D AND TABLE E
EN1-PS1
PDU A1-4
EN1-PS1
PDU A1-4
LABEL CABLE AS SHOWN IN TABLE A AND TABLE B.
LABEL PN 658-0785-01 (LOCATE APPROX AS SHOWN)

## 870-3103-01_Component Labeling
General Labeling Notes
1) Rack Mount Servers position are to be labeled on the front and rear mounting rails as shown in Fig 42 and Fig 43. This is typical for all servers. (i.e. SERVER A)
2) The Cisco 4948E-F switches are to be labeled on the left hand side mounting rail (front and rear) using 7300465. See Figure 44 and 45.
3) All power and data cables shall be labeled as shown in Figures 14 and 15. The "FROM/TO" detail is shown on the POWER AND DATA Cable tabs of this document. There are two labels on each cable. The "TO" portion of the label goes on the end of the cable that is attaching "TO" that destination.
4) Equipment code abbreviations are as follows: ● Cabinet designation - Cx - where x is the cabinet number in the EAGLE XG line-up (1-x) ● c7000 enclosure - eny - where y is the enclosure number in the cabinet (1-2) ● Cisco Aggregation switch - agx - where x is the switch number (A/B) ● Server blade - bayx - where x is the bay number of the server (1-16) ● Ethernet blade switch - swx - where x is the I/O bay location (1-8) ● OAx - where x is the number of the Onboard Administrator (OA1 - left from rear; OA2- right from rear) ● SERVER X - where X is the letter of the Server (starting with SERVER A)
5) Cable Label Text height shall be .06-.12 high; text in contrasting color to label.
6) PDUS should be labeled on the front face of the PDU module using label PN 617-0009-01 approx shown in Figure 32. Trim clear portion of this label off prior to applying it to the cabinet. Text height should be .20 +/-.06.
7) Label front door as shown in Figure 35. Label is part of the 870-3103-01 BOM.
8) Consolidated label part of 870-3103-01 BOM. Locate as shown in Figure 36 and apply associated labels as shown in Detail B.
9) Use7300465 to label all components as required in the cabinet. Use the labels from Column C to label the servers and switches. See Figure 41 for label format.
FIGURE 32: PDU LABELING
SEE GENERAL LABELING NOTE 6
FIGURE 33 : CABLE LABELING FOR C7000 ENCLSOURE
(SEE ASSY NOTE 13 AND GENERAL LABELING NOTE 3 AND 5)
FIGURE 34: CABLE LABELING FOR SERVERS | SEE ASSEMBLY NOTE 12
(SEE ASSY NOTE 13 AND GENERAL LABELING NOTE 3 AND 5)
FIGURE 35 : FRONT DOOR LABELING
(SEE GENERAL LABELING NOTE 7)
FIGURE 36: CONSOLIDATED LABEL DETAILS
(SEE ASSEMBLY NOTE 15 AND GENERAL LABELING NOTE 8)
FIGURE 37: 1U AND/OR 2U SERVER AND SWITCH DESIGNATIONS 44U WRIGHT LINE CABINET WITH ONE c7000 ENCLSOURE
805-0585-01 OR 805-0582-01
|  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
| SWITCH B | 44
43
| SWITCH A | 42
41
|  | 40 | SERVER A DL380 - (805-0608-XX) | SERVER A HP DL360/ORACLE X5-2
|  | 39 |  | SERVER B HP DL360/ORACLE X5-2
|  | 38 | SERVER B DL380 - (805-0608-XX) | SERVER C HP DL360/ORACLE X5-2
|  | 37 |  | SERVER D HP DL360/ORACLE X5-2
|  | 36 | SERVER C DL380 - (805-0608-XX) | SERVER E HP DL360/ORACLE X5-2
|  | 35 |  | SERVER F HP DL360/ORACLE X5-2
|  | 34 | SERVER D DL380 - (805-0608-XX) | SERVER G HP DL360/ORACLE X5-2
|  | 33 |  | SERVER H HP DL360/ORACLE X5-2
|  | 32 | SERVER E DL380 - (805-0608-XX) | SERVER I HP DL360/ORACLE X5-2
|  | 31 |  | SERVER J HP DL360/ORACLE X5-2
|  | 30 | SERVER F DL380 - (805-0608-XX) | SERVER K HP DL360/ORACLE X5-2
|  | 29 |  | SERVER L HP DL360/ORACLE X5-2
|  | 28 | SERVER G DL380 - (805-0608-XX) | NOT USED
|  | 27 |  | NOT USED
|  | 26 | SERVER H DL380 - (805-0608-XX) | NOT USED
|  | 25 |  | NOT USED
|  | 24 | SERVER I DL380 - (805-0608-XX) | NOT USED
|  | 23 |  | NOT USED
|  | 22 | SERVER J DL380 - (805-0608-XX) | NOT USED
|  | 21 |  | NOT USED
|  | 20 | SERVER K DL380 - (805-0608-XX) | NOT USED
|  | 19 |  | NOT USED
|  | 18 | SERVER L DL380 - (805-0608-XX) | NOT USED
|  | 17 |  | NOT USED
|  | 16 | FILLER PANEL
|  | 15 | FILLER PANEL
|  | 14 | SEISMIC BRACE 805-0188-G01
FIGURE 38: 1U AND/OR 2U SERVER AND SWITCH DESIGNATIONS 40U WRIGHT LINE CABINET WITH ONE c7000 ENCLSOURE
805-0583-01 OR 805-0562-01
|  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
| SWITCH B | 40
39
| SWITCH A | 38
37
|  | 36 | SERVER A DL380 - (805-0608-XX) | SERVER A HP DL360/ORACLE X5-2
|  | 35 |  | SERVER B HP DL360/ORACLE X5-2
|  | 34 | SERVER B DL380 - (805-0608-XX) | SERVER C HP DL360/ORACLE X5-2
|  | 33 |  | SERVER D HP DL360/ORACLE X5-2
|  | 32 | SERVER C DL380 - (805-0608-XX) | SERVER E HP DL360/ORACLE X5-2
|  | 31 |  | SERVER F HP DL360/ORACLE X5-2
|  | 30 | SERVER D DL380 - (805-0608-XX) | SERVER G HP DL360/ORACLE X5-2
|  | 29 |  | SERVER H HP DL360/ORACLE X5-2
|  | 28 | SERVER E DL380 - (805-0608-XX) | SERVER I HP DL360/ORACLE X5-2
|  | 27 |  | SERVER J HP DL360/ORACLE X5-2
|  | 26 | SERVER F DL380 - (805-0608-XX) | SERVER K HP DL360/ORACLE X5-2
|  | 25 |  | SERVER L HP DL360/ORACLE X5-2
|  | 24 | SERVER G DL380 - (805-0608-XX) | NOT USED
|  | 23 |  | NOT USED
|  | 22 | SERVER H DL380 - (805-0608-XX) | NOT USED
|  | 21 |  | NOT USED
|  | 20 | SERVER I DL380 - (805-0608-XX) | NOT USED
|  | 19 |  | NOT USED
|  | 18 | SERVER J DL380 - (805-0608-XX) | NOT USED
|  | 17 |  | NOT USED
|  | 16 | SERVER K DL380 - (805-0608-XX) | NOT USED
|  | 15 |  | NOT USED
|  | 14 | SEISMIC BRACE 805-0188-G01
FIGURE 39: 1U AND/OR 2U SERVER AND SWITCH DESIGNATIONS 44U WRIGHT LINE CABINET WITH TWO c7000 ENCLSOURE
805-0585-01 OR 805-0582-01
|  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
| SWITCH B | 44
43
| SWITCH A | 42
41
|  | 40 | SERVER A DL380 - (805-0608-XX) | SERVER A HP DL360/ORACLE X5-2
|  | 39 |  | SERVER B HP DL360/ORACLE X5-2
|  | 38 | SERVER B DL380 - (805-0608-XX) | SERVER C HP DL360/ORACLE X5-2
|  | 37 |  | NOT USED
|  | 36 | SERVER C DL380 - (805-0608-XX) | NOT USED
|  | 35 |  | NOT USED
|  | 34 | FILLER PANEL
|  | 33 | FILLER PANEL
|  | 32 | FILLER PANEL
|  | 31 | FILLER PANEL
|  | 30 | FILLER PANEL
|  | 29 | FILLER PANEL
|  | 28 | FILLER PANEL
|  | 27 | FILLER PANEL
|  | 26 | FILLER PANEL
|  | 25 | SEISMIC BRACE 805-0188-G01
FIGURE 40: 1U AND/OR 2U SERVER AND SWITCH DESIGNATIONS 40U WRIGHT LINE CABINET WITH TWO c7000 ENCLSOURE
805-0583-01 OR 805-0562-01
|  | RACK U | Eagle XG c-Class Cabinet (Max config) 870-3103-01
| SWITCH B | 40
39
| SWITCH A | 38
37
|  | 36 | SERVER A DL380 - (805-0608-XX) | SERVER A HP DL360/ORACLE X5-2
|  | 35 |  | SERVER B HP DL360/ORACLE X5-2
|  | 34 | SERVER B DL380 - (805-0608-XX) | SERVER C HP DL360/ORACLE X5-2
|  | 33 |  | NOT USED
|  | 32 | SERVER C DL380 - (805-0608-XX) | NOT USED
|  | 31 |  | NOT USED
|  | 30 | FILLER PANEL
|  | 29 | FILLER PANEL
|  | 28 | FILLER PANEL
|  | 27 | FILLER PANEL
|  | 26 | FILLER PANEL
|  | 25 | SEISMIC BRACE 805-0188-G01
FIGURE 41: CABINET LABEL
SEE GENERAL LABELING NOTE 9
7300465 Label Set use the labels from Column C to label the servers and switches.
FIGURE 42: CABINET LABELING -DL380 GEN9 SERVERS FRONT RAIL
SEE GENERAL LABELING NOTE 1
FIGURE 43: CABINET LABELING -TYPICAL SERVERS LABELING REAR RAIL
SEE GENERAL LABELING NOTE 1
FIGURE 44: CABINET LABELING 4948E-F SWITCHES- FRONT RAIL
SEE GENERAL LABELING NOTE 2
FIGURE 45: CABINET LABELING 4948E-F SWITCHES- REAR RAIL
SEE GENERAL LABELING NOTE 2
MOUNT THE PDU's WITH THE INPUT POWER CABLE EXITING TOWARDS THE BOTTOM. UNLESS OTHERWISE SPECIFIED. LABEL CABLES AS SHOWN IN POWER TABLE. SECURE CABLES TO PREVENT DAMAGE DURING SHIPPING USING HOOK AND LOOP OR WAXED LACING CORD (SEE ASSEMBLY NOTE 28).
658-0785-01 Anti Static Label
Locate label 2.00 inches below door handle and align the left edge with the door frame +/-.25
PDU A
PDU B
REAR VIEW-PDU LOCATION
LABEL THE 50AMP PDU WRIGHT LINE PN 17110314 APPROX AS SHOWN. LABEL PN 617-0009-01
FROM
SERVER X PORT X
TO
SWITCH X PORT XX
FROM
SWITCH X PORT XX
TO
SERVER X PORT X
CISCO 4948E-F SWITCH (FRONT VIEW)
CONSOLIDATED SYSTEM LABEL
658-0770-11
(Note: Logo at top)
See Detail B for additional details.
Detail B
7300465 Label Set use the labels from Column C to label the servers and switches.
NOTE:
IF THE 1U AND 2U SERVERS ARE MIXED IN THE CABINET THEN INSTALL THE 2U SERVERS FIRST STARTING IN "SERVER A" POSITION. AFTER ALL THE 2U SERVERS ARE INSTALLED START INSTALLING THE 1U SERVERS IN THE NEXT AVAILABLE "RACK U" LEAVING NO SPACE BETWEEN SERVERS. THE SERVERS WILL BE LABELED FROM THE TOP DOWN STARTING WITH SERVER A AND LABELING EACH SERVER WITH THE NEXT LETTER (SERVER A-L). MAX CONFIGURATION FOR SERVERS IS 12 IF THE CABINET HAS ONLY ONE C7000 ENCLOSURE.
NOTE:
IF THE 1U AND 2U SERVERS ARE MIXED IN THE CABINET THEN INSTALL THE 2U SERVERS FIRST STARTING IN "SERVER A" POSITION. AFTER ALL THE 2U SERVERS ARE INSTALLED START INSTALLING THE 1U SERVERS IN THE NEXT AVAILABLE "RACK U" LEAVING NO SPACE BETWEEN SERVERS. THE SERVERS WILL BE LABELED FROM THE TOP DOWN STARTING WITH SERVER A AND LABELING EACH SERVER WITH THE NEXT LETTER (SERVER A-L). MAX CONFIGURATION FOR SERVERS IS 12 x 1U SERVERS OR 11 x 2U SERVERS IF THE CABINET HAS ONE C7000 ENCLOSURE.
NOTE:
IF THE 1U AND 2U SERVERS ARE MIXED IN THE CABINET THEN INSTALL THE 2U SERVERS FIRST STARTING IN "SERVER A" POSITION. AFTER ALL THE 2U SERVERS ARE INSTALLED START INSTALLING THE 1U SERVERS IN THE NEXT AVAILABLE "RACK U" LEAVING NO SPACE BETWEEN SERVERS. THE SERVERS WILL BE LABELED FROM THE TOP DOWN STARTING WITH SERVER A AND LABELING EACH SERVER WITH THE NEXT LETTER (SERVER A-C). MAX CONFIGURATION FOR SERVERS IS 3 x 1U SERVERS OR 3 x 2U SERVERS IF THE CABINET HAS TWO C7000 ENCLOSURES.
NOTE:
IF THE 1U AND 2U SERVERS ARE MIXED IN THE CABINET THEN INSTALL THE 2U SERVERS FIRST STARTING IN "SERVER A" POSITION. AFTER ALL THE 2U SERVERS ARE INSTALLED START INSTALLING THE 1U SERVERS IN THE NEXT AVAILABLE "RACK U" LEAVING NO SPACE BETWEEN SERVERS. THE SERVERS WILL BE LABELED FROM THE TOP DOWN STARTING WITH SERVER A AND LABELING EACH SERVER WITH THE NEXT LETTER (SERVER A-C). MAX CONFIGURATION FOR SERVERS IS 3 x 1U SERVERS OR 3 x 2U SERVERS IF THE CABINET HAS TWO C7000 ENCLOSURES.
7300465 Label Set use the labels from Column C to label the servers and switches.
CISCO 4948E-F SWITCH (FRONT VIEW)
7300465 Label Set use the labels from Column C to label the servers and switches.
7300465 Label Set use the labels from Column C to label the servers and switches.
870-3103-01_Component Labeling Tab
LABEL THE 50AMP PDU WRIGHT LINE PN VZIAN21650IPB APPROX AS SHOWN. LABEL PN 617-0009-01.
PDU PWR CORD EXITS THIS SIDE ON BOTTOM

## 870-3111-01_Single Ph Pwr Cable
870-3111-01_SINGLE PHASE POWER CABLES Tab
TABLE B: SINGLE PHASE POWER CABLES - EAGLE XG CABINET WITH THREE ENCLOSURES/TWO (2) CISCO 4948E-F/ONE (1) DL380 2U SERVER OR (2) DL360 **See 892-0125-01 Detail B System Interconnect NOTE: The following table will only apply if the end user has purchased the HP Power Panels (See Pick List for PN and more details)
CABLE PN | CABLE NUMBER | FROM | TO | LABEL REQUIRED
830-1903-02 | 30 | SWITCH B-A PWR | PDU A1-4 POS 7 | YES
830-1903-02 | 31 | SWITCH B-B PWR | PDU B1-4 POS 7 | YES
830-1903-02 | 32 | SWITCH A-A PWR | PDU A1-4 POS 5 | YES
830-1903-02 | 33 | SWITCH A-B PWR | PDU B1-4 POS 5 | YES
Power Cable (Note 1) | 34 | SERVER A – A PWR | PDU A1-4 POS 3 | YES
Power Cable (Note 1) | 35 | SERVER A – B PWR | PDU B1-4 POS 3 | YES
Power Cable (Note 1) | 36 | SERVER B – A PWR | PDU A3-4 POS 7 | YES
Power Cable (Note 1) | 37 | SERVER B – B PWR | PDU B3-4 POS 7 | YES
HARD WIRED | 25 | PDU B3-4 | PDU B3 POS 4 | YES
Power Cable (Note 1) | 18 | CXEN3-PS6 | PDU B3 POS 3 | YES
Power Cable (Note 1) | 17 | CXEN3-PS5 | PDU B3 POS 2 | YES
Power Cable (Note 1) | 16 | CXEN3-PS4 | PDU B3 POS 1 | YES
HARD WIRED | 24 | PDU A3-4 | PDU A3 POS 4 | YES
Power Cable (Note 1) | 15 | CXEN3-PS3 | PDU A3 POS 3 | YES
Power Cable (Note 1) | 14 | CXEN3-PS2 | PDU A3 POS 2 | YES
Power Cable (Note 1) | 13 | CXEN3-PS1 | PDU A3 POS 1 | YES
N/A | N/A | EMPTY | PDU B2 POS 4 | N/A
Power Cable (Note 1) | 12 | CXEN2-PS6 | PDU B2 POS 3 | YES
Power Cable (Note 1) | 11 | CXEN2-PS5 | PDU B2 POS 2 | YES
Power Cable (Note 1) | 10 | CXEN2-PS4 | PDU B2 POS 1 | YES
N/A | N/A | EMPTY | PDU A2 POS 4 | N/A
Power Cable (Note 1) | 9 | CXEN2-PS3 | PDU A2 POS 3 | YES
Power Cable (Note 1) | 8 | CXEN2-PS2 | PDU A2 POS 2 | YES
Power Cable (Note 1) | 7 | CXEN2-PS1 | PDU A2 POS 1 | YES
HARD WIRED | 21 | PDU B1-4 | PDU B1 POS 4 | YES
Power Cable (Note 1) | 6 | CXEN1-PS6 | PDU B1 POS 3 | YES
Power Cable (Note 1) | 5 | CXEN1-PS5 | PDU B1 POS 2 | YES
Power Cable (Note 1) | 4 | CXEN1-PS4 | PDU B1 POS 1 | YES
HARD WIRED | 20 | PDU A1-4 | PDU A1 POS 4 | YES
Power Cable (Note 1) | 3 | CXEN1-PS3 | PDU A1 POS 3 | YES
Power Cable (Note 1) | 2 | CXEN1-PS2 | PDU A1 POS 2 | YES
Power Cable (Note 1) | 1 | CXEN1-PS1 | PDU A1 POS 1 | YES
Cable attached | 19 | PDU A1 | Facility power | YES
Cable attached | 19 | PDU A2 | Facility power | YES
Cable attached | 19 | PDU B1 | Facility power | YES
Cable attached | 19 | PDU B2 | Facility power | YES
Cable attached | 19 | PDU A3 | Facility power | YES
Cable attached | 19 | PDU B3 | Facility power | YES
NOTE 1: Power cables are supplied with each component.
TABLE C: SINGLE PHASE POWER CABLES - EAGLE XG CABINET WITH ONE (1) OR TWO (2) ENCLOSURES/TWO CISCO 4948E-F/UP TO TWELVE (12) RMS *See 892-0125-01 Detail D System Interconnect NOTE: The following table will only apply if the end user has purchased the HP Power Panels (See Pick List for PN and more details)
CABLE PN | CABLE NUMBER | FROM | TO | LABEL REQUIRED
830-1903-02 | 30 | SWITCH B-A PWR | PDU A1-4 POS 7 | YES
830-1903-02 | 31 | SWITCH B-B PWR | PDU B1-4 POS 7 | YES
830-1903-02 | 32 | SWITCH A-A PWR | PDU A1-4 POS 5 | YES
830-1903-02 | 33 | SWITCH A-B PWR | PDU B1-4 POS 5 | YES
Power Cable (Note 1) | 34 | SERVER A – A PWR | PDU A1-4 POS 3 | YES
Power Cable (Note 1) | 35 | SERVER A – B PWR | PDU B1-4 POS 3 | YES
Power Cable (Note 1) | 36 | SERVER B – A PWR | PDU A3-4 POS 7 | YES
Power Cable (Note 1) | 37 | SERVER B – B PWR | PDU B3-4 POS 7 | YES
Power Cable (Note 1) | 38 | SERVER C - A PWR | PDU A3-4 POS 6 | YES
Power Cable (Note 1) | 39 | SERVER C - B PWR | PDU B3-4 POS 6 | YES
Power Cable (Note 1) | 40 | SERVER D - A PWR | PDU A3-4 POS 5 | YES
Power Cable (Note 1) | 41 | SERVER D - B PWR | PDU B3-4 POS 5 | YES
Power Cable (Note 1) | 42 | SERVER E - A PWR | PDU A3-4 POS 4 | YES
Power Cable (Note 1) | 43 | SERVER E - B PWR | PDU B3-4 POS 4 | YES
Power Cable (Note 1) | 44 | SERVER F - A PWR | PDU A3-4 POS 3 | YES
Power Cable (Note 1) | 45 | SERVER F - B PWR | PDU B3-4 POS 3 | YES
Power Cable (Note 1) | 46 | SERVER G - A PWR | PDU A3-4 POS 2 | YES
Power Cable (Note 1) | 47 | SERVER G - B PWR | PDU B3-4 POS 2 | YES
Power Cable (Note 1) | 48 | SERVER H - A PWR | PDU A3-3 POS 1 | YES
Power Cable (Note 1) | 49 | SERVER H - B PWR | PDU B3-3 POS 1 | YES
Power Cable (Note 1) | 50 | SERVER I - A PWR | PDU A3-3 POS 2 | YES
Power Cable (Note 1) | 51 | SERVER I - B PWR | PDU B3-3 POS 2 | YES
Power Cable (Note 1) | 52 | SERVER J - A PWR | PDU A3-3 POS 3 | YES
Power Cable (Note 1) | 53 | SERVER J - B PWR | PDU B3-3 POS 3 | YES
Power Cable (Note 1) | 54 | SERVER K - A PWR | PDU A3-3 POS 4 | YES
Power Cable (Note 1) | 55 | SERVER K - B PWR | PDU B3-3 POS 4 | YES
Power Cable (Note 1) | 56 | SERVER L - A PWR | PDU A3-3 POS 5 | YES
Power Cable (Note 1) | 57 | SERVER L - B PWR | PDU B3-3 POS 5 | YES
HARD WIRED | 25 | PDU B3-4 | PDU B3 POS 4 | YES
HARD WIRED | 24 | PDU B3-3 | PDU B3 POS 3 | YES
N/A | N/A | EMPTY | PDU B3 POS 2 | N/A
N/A | N/A | EMPTY | PDU B3 POS 1 | N/A
HARD WIRED | 23 | PDU A3-4 | PDU A3 POS 4 | YES
HARD WIRED | 22 | PDU A3-3 | PDU A3 POS 3 | YES
N/A | N/A | EMPTY | PDU A3 POS 2 | N/A
N/A | N/A | EMPTY | PDU A3 POS 1 | N/A
N/A | N/A | EMPTY | PDU B2 POS 4 | N/A
Power Cable (Note 1) | 12 | CXEN2-PS6 | PDU B2 POS 3 | YES
Power Cable (Note 1) | 11 | CXEN2-PS5 | PDU B2 POS 2 | YES
Power Cable (Note 1) | 10 | CXEN2-PS4 | PDU B2 POS 1 | YES
N/A | N/A | EMPTY | PDU A2 POS 4 | N/A
Power Cable (Note 1) | 9 | CXEN2-PS3 | PDU A2 POS 3 | YES
Power Cable (Note 1) | 8 | CXEN2-PS2 | PDU A2 POS 2 | YES
Power Cable (Note 1) | 7 | CXEN2-PS1 | PDU A2 POS 1 | YES
HARD WIRED | 21 | PDU B1-4 | PDU B1 POS 4 | YES
Power Cable (Note 1) | 6 | CXEN1-PS6 | PDU B1 POS 3 | YES
Power Cable (Note 1) | 5 | CXEN1-PS5 | PDU B1 POS 2 | YES
Power Cable (Note 1) | 4 | CXEN1-PS4 | PDU B1 POS 1 | YES
HARD WIRED | 20 | PDU A1-4 | PDU A1 POS 4 | YES
Power Cable (Note 1) | 3 | CXEN1-PS3 | PDU A1 POS 3 | YES
Power Cable (Note 1) | 2 | CXEN1-PS2 | PDU A1 POS 2 | YES
Power Cable (Note 1) | 1 | CXEN1-PS1 | PDU A1 POS 1 | YES
Cable attached | 19 | PDU A1 | Facility power | YES
Cable attached | 19 | PDU A2 | Facility power | YES
Cable attached | 19 | PDU B1 | Facility power | YES
Cable attached | 19 | PDU B2 | Facility power | YES
Cable attached | 19 | PDU A3 | Facility power | YES
Cable attached | 19 | PDU B3 | Facility power | YES
NOTE 1: Power cables are supplied with each component.

## 870-3111-01_3 Ph Pwr Cables
870-3111-01_THREE PHASE POWER CABLES Tab
TABLE D: THREE PHASE POWER CABLES - EAGLE XG CABINET WITH THREE ENCLOSURES/TWO (2) CISCO 4948E-F/ (1) DL380 2U SERVER OR (2) DL360 **See 892-0125-01 Detail A System Interconnect NOTE: The following table will only apply if the end user has purchased the HP Power Panels (See Pick List for PN and more details)
CABLE PN | CABLE NUMBER | FROM | TO | LABEL REQUIRED
830-1903-02 | 30 | SWITCH B-A PWR | PDU A1-6 POS 7 | YES
830-1903-02 | 31 | SWITCH B-B PWR | PDU B1-6 POS 7 | YES
830-1903-02 | 32 | SWITCH A-A PWR | PDU A1-5 POS 7 | YES
830-1903-02 | 33 | SWITCH A-B PWR | PDU B1-5 POS 7 | YES
Power Cable (Note 1) | 34 | SERVER A – A PWR | PDU A1-5 POS 5 | YES
Power Cable (Note 1) | 35 | SERVER A – B PWR | PDU B1-5 POS 5 | YES
Power Cable (Note 1) | 36 | SERVER B – A PWR | PDU A1-6 POS 5 | YES
Power Cable (Note 1) | 37 | SERVER B – B PWR | PDU B1-6 POS 5 | YES
Power Cable (Note 1) | 18 | CXEN3-PS6 | PDU B2 - L5 | YES
Power Cable (Note 1) | 17 | CXEN3-PS5 | PDU B2 - L4 | YES
Power Cable (Note 1) | 16 | CXEN3-PS4 | PDU B1 - L4 | YES
Power Cable (Note 1) | 15 | CXEN3-PS3 | PDU A2 - L5 | YES
Power Cable (Note 1) | 14 | CXEN3-PS2 | PDU A2 - L4 | YES
Power Cable (Note 1) | 13 | CXEN3-PS1 | PDU A1 - L4 | YES
Power Cable (Note 1) | 12 | CXEN2-PS6 | PDU B2 - L3 | YES
Power Cable (Note 1) | 11 | CXEN2-PS5 | PDU B2 - L2 | YES
Power Cable (Note 1) | 10 | CXEN2-PS4 | PDU B2 - L1 | YES
Power Cable (Note 1) | 9 | CXEN2-PS3 | PDU A2 - L3 | YES
Power Cable (Note 1) | 8 | CXEN2-PS2 | PDU A2 - L2 | YES
Power Cable (Note 1) | 7 | CXEN2-PS1 | PDU A2 - L1 | YES
HARD WIRED | 29 | PDU B1-6 | PDU B1 - L6 | YES
HARD WIRED | 28 | PDU B1-5 | PDU B1 - L5 | YES
Power Cable (Note 1) | 6 | CXEN1-PS6 | PDU B1 - L3 | YES
Power Cable (Note 1) | 5 | CXEN1-PS5 | PDU B1 - L2 | YES
Power Cable (Note 1) | 4 | CXEN1-PS4 | PDU B1 - L1 | YES
HARD WIRED | 27 | PDU A1-6 | PDU A1 - L6 | YES
HARD WIRED | 26 | PDU A1-5 | PDU A1 - L5 | YES
Power Cable (Note 1) | 3 | CXEN1-PS3 | PDU A1 - L3 | YES
Power Cable (Note 1) | 2 | CXEN1-PS2 | PDU A1 - L2 | YES
Power Cable (Note 1) | 1 | CXEN1-PS1 | PDU A1 - L1 | YES
Cable attached | 19 | PDU A1 | Facility power | YES
Cable attached | 19 | PDU A2 | Facility power | YES
Cable attached | 19 | PDU B1 | Facility power | YES
Cable attached | 19 | PDU B2 | Facility power | YES
NOTE 1: Power cables are supplied with each component.
TABLE E: THREE PHASE POWER CABLES - EAGLE XG CABINET WITH ONE (1) OR TWO (2) ENCLOSURES/TWO CISCO 4948E-F/ UP TO TWELVE (12) RMS **See 892-0125-01 Detail C System Interconnect NOTE: The following table will only apply if the end user has purchased the HP Power Panels (See Pick List for PN and more details)
CABLE PN | CABLE NUMBER | FROM | TO | LABEL REQUIRED
830-1903-02 | 30 | SWITCH B-A PWR | PDU A1-6 POS 7 | YES
830-1903-02 | 31 | SWITCH B-B PWR | PDU B1-6 POS 7 | YES
830-1903-02 | 32 | SWITCH A-A PWR | PDU A1-5 POS 7 | YES
830-1903-02 | 33 | SWITCH A-B PWR | PDU B1-5 POS 7 | YES
Power Cable (Note 1) | 34 | SERVER A – A PWR | PDU A1-5 POS 5 | YES
Power Cable (Note 1) | 35 | SERVER A – B PWR | PDU B1-5 POS 5 | YES
Power Cable (Note 1) | 36 | SERVER B – A PWR | PDU A1-6 POS 5 | YES
Power Cable (Note 1) | 37 | SERVER B – B PWR | PDU B1-6 POS 5 | YES
Power Cable (Note 1) | 38 | SERVER C - A PWR | PDU A1-4 POS 7 | YES
Power Cable (Note 1) | 39 | SERVER C - B PWR | PDU B1-4 POS 7 | YES
Power Cable (Note 1) | 40 | SERVER D - A PWR | PDU A1-4 POS 6 | YES
Power Cable (Note 1) | 41 | SERVER D - B PWR | PDU B1-4 POS 6 | YES
Power Cable (Note 1) | 42 | SERVER E - A PWR | PDU A1-6 POS 3 | YES
Power Cable (Note 1) | 43 | SERVER E - B PWR | PDU B1-6 POS 3 | YES
Power Cable (Note 1) | 44 | SERVER F - A PWR | PDU A1-5 POS 3 | YES
Power Cable (Note 1) | 45 | SERVER F - B PWR | PDU B1-5 POS 3 | YES
Power Cable (Note 1) | 46 | SERVER G - A PWR | PDU A1-4 POS 5 | YES
Power Cable (Note 1) | 47 | SERVER G - B PWR | PDU B1-4 POS 5 | YES
Power Cable (Note 1) | 48 | SERVER H - A PWR | PDU A1-6 POS 1 | YES
Power Cable (Note 1) | 49 | SERVER H - B PWR | PDU B1-6 POS 1 | YES
Power Cable (Note 1) | 50 | SERVER I - A PWR | PDU A1-5 POS 1 | YES
Power Cable (Note 1) | 51 | SERVER I - B PWR | PDU B1-5 POS 1 | YES
Power Cable (Note 1) | 52 | SERVER J - A PWR | PDU A1-4 POS 4 | YES
Power Cable (Note 1) | 53 | SERVER J - B PWR | PDU B1-4 POS 4 | YES
Power Cable (Note 1) | 54 | SERVER K - A PWR | PDU A1-4 POS 3 | YES
Power Cable (Note 1) | 55 | SERVER K - B PWR | PDU B1-4 POS 3 | YES
Power Cable (Note 1) | 56 | SERVER L - A PWR | PDU A1-4 POS 2 | YES
Power Cable (Note 1) | 57 | SERVER L - B PWR | PDU B1-4 POS 2 | YES
Power Cable (Note 1) | 12 | CXEN2-PS6 | PDU B2 - L3 | YES
Power Cable (Note 1) | 11 | CXEN2-PS5 | PDU B2 - L2 | YES
Power Cable (Note 1) | 10 | CXEN2-PS4 | PDU B2 - L1 | YES
Power Cable (Note 1) | 9 | CXEN2-PS3 | PDU A2 - L3 | YES
Power Cable (Note 1) | 8 | CXEN2-PS2 | PDU A2 - L2 | YES
Power Cable (Note 1) | 7 | CXEN2-PS1 | PDU A2 - L1 | YES
HARD WIRED | 29 | PDU B1-6 | PDU B1 - L6 | YES
HARD WIRED | 28 | PDU B1-5 | PDU B1 - L5 | YES
HARD WIRED | 61 | PDU B1-4 | PDU B1 - L4 | YES
Power Cable (Note 1) | 6 | CXEN1-PS6 | PDU B1 - L3 | YES
Power Cable (Note 1) | 5 | CXEN1-PS5 | PDU B1 - L2 | YES
Power Cable (Note 1) | 4 | CXEN1-PS4 | PDU B1 - L1 | YES
HARD WIRED | 27 | PDU A1-6 | PDU A1 - L6 | YES
HARD WIRED | 26 | PDU A1-5 | PDU A1 - L5 | YES
HARD WIRED | 60 | PDU A1-4 | PDU A1 - L4 | YES
Power Cable (Note 1) | 3 | CXEN1-PS3 | PDU A1 - L3 | YES
Power Cable (Note 1) | 2 | CXEN1-PS2 | PDU A1 - L2 | YES
Power Cable (Note 1) | 1 | CXEN1-PS1 | PDU A1 - L1 | YES
Cable attached | 19 | PDU A1 | Facility power | YES
Cable attached | 19 | PDU A2 | Facility power | YES
Cable attached | 19 | PDU B1 | Facility power | YES
Cable attached | 19 | PDU B2 | Facility power | YES
NOTE 1: Power cables are supplied with each component.

## 870-3103-01_Power Cables
TABLE K: POWER CABLES for use with Wright Line PDU 17110314 50 AMP PDU MAX Configuration is 2 enclosures and three servers or one enclosure and 12 servers. See 892-0119-01 System Interconnect. NOTE: The following table will only apply if the end user has purchased the Wright Line Power Panels (See 870-3103-01 Pick List for PN and more details)
CABLE NUMBER | CABLE PN | FROM | TO | LABEL REQUIRED
101 | 804-1106-04 | CXEN1-PS1 | PDU A-CIRCUIT 1-POS 3 | YES
102 | 804-1106-04 | CXEN1-PS2 | PDU A-CIRCUIT 2-POS 6 | YES
103 | 804-1106-04 | CXEN1-PS3 | PDU A-CIRCUIT 3-POS 9 | YES
104 | 804-1106-03 | CXEN1-PS4 | PDU B-CIRCUIT 1-POS 3 | YES
105 | 804-1106-03 | CXEN1-PS5 | PDU B-CIRCUIT 2-POS 6 | YES
106 | 804-1106-03 | CXEN1-PS6 | PDU B-CIRCUIT 3-POS 9 | YES
107 | 804-1106-04 | CXEN2-PS1 | PDU A-CIRCUIT 1-POS 6 | YES
108 | 804-1106-04 | CXEN2-PS2 | PDU A-CIRCUIT 2-POS 9 | YES
109 | 804-1106-04 | CXEN2-PS3 | PDU A-CIRCUIT 3-POS 3 | YES
110 | 804-1106-03 | CXEN2-PS4 | PDU B-CIRCUIT 1-POS 6 | YES
111 | 804-1106-03 | CXEN2-PS5 | PDU B-CIRCUIT 2-POS 9 | YES
112 | 804-1106-03 | CXEN2-PS6 | PDU B-CIRCUIT 3-POS 3 | YES
113-118 | NOT USED
119 | 804-0053-02 | SERVER A - A PWR | PDU A-CIRCUIT 3-POS 8 | YES
120 | 804-0053-01 | SERVER A - B PWR | PDU B-CIRCUIT 3-POS 8 | YES
121 | 804-0053-04 | SERVER B - A PWR | PDU A-CIRCUIT 2-POS 5 | YES
122 | 804-0053-03 | SERVER B - B PWR | PDU B-CIRCUIT 2-POS 5 | YES
123 | 804-0053-04 | SERVER C - A PWR | PDU A-CIRCUIT 1-POS 1 | YES
124 | 804-0053-03 | SERVER C - B PWR | PDU B-CIRCUIT 1-POS 1 | YES
125 | 804-0053-04 | SERVER D - A PWR | PDU A-CIRCUIT 3-POS 2 | YES
126 | 804-0053-03 | SERVER D - B PWR | PDU B-CIRCUIT 3-POS 2 | YES
127 | 804-0053-04 | SERVER E - A PWR | PDU A-CIRCUIT 2-POS 8 | YES
128 | 804-0053-03 | SERVER E - B PWR | PDU B-CIRCUIT 2-POS 8 | YES
129 | 804-0053-04 | SERVER F - A PWR | PDU A-CIRCUIT 1-POS 4 | YES
130 | 804-0053-03 | SERVER F - B PWR | PDU B-CIRCUIT 1-POS 4 | YES
131 | 804-0053-04 | SERVER G - A PWR | PDU A-CIRCUIT 3-POS 5 | YES
132 | 804-0053-03 | SERVER G - B PWR | PDU B-CIRCUIT 3-POS 5 | YES
133 | 804-0053-04 | SERVER H - A PWR | PDU A-CIRCUIT 2-POS 2 | YES
134 | 804-0053-03 | SERVER H - B PWR | PDU B-CIRCUIT 2-POS 2 | YES
135 | 804-0053-04 | SERVER I - A PWR | PDU A-CIRCUIT 1-POS 7 | YES
136 | 804-0053-03 | SERVER I - B PWR | PDU B-CIRCUIT 1-POS 7 | YES
137 | 804-0053-04 | SERVER J - A PWR | PDU A-CIRCUIT 3-POS 4 | YES
138 | 804-0053-03 | SERVER J - B PWR | PDU B-CIRCUIT 3-POS 4 | YES
139 | 804-0053-04 | SERVER K - A PWR | PDU A-CIRCUIT 2-POS 1 | YES
140 | 804-0053-03 | SERVER K - B PWR | PDU B-CIRCUIT 2-POS 1 | YES
141 | 804-0053-04 | SERVER L - A PWR | PDU A-CIRCUIT 2-POS 7 | YES
142 | 804-0053-03 | SERVER L - B PWR | PDU B-CIRCUIT 2-POS 7 | YES
143 | 804-0053-04 | SWITCH A - A PWR | PDU A-CIRCUIT 3-POS 7 | YES
144 | 804-0053-03 | SWITCH A - B PWR | PDU B-CIRCUIT 3-POS 7 | YES
145 | 804-0053-04 | SWITCH B - A PWR | PDU A-CIRCUIT 2-POS 4 | YES
146 | 804-0053-03 | SWITCH B - B PWR | PDU B-CIRCUIT 2-POS 4 | YES
147 | See Note 1 below | PDU A | FACILITY POWER | YES
148 | See Note 1 below | PDU B | FACILITY POWER | YES
NOTE 1: Main power input cables are supplied with the PDU units. Input Connector is a 10ft power cord with California Style 50 Amp, 250 Volt, 4 wire Twistlock Plug.
TABLE L: POWER CABLES 30 AMP PDU MAX Configuration is 2 enclosures and three servers or one enclosure and 12 servers. See 892-0119-01 System Interconnect NOTE: The following table will only apply if the end user has purchased the Wright Line Power Panels (See 870-3103-01 Pick List for PN and more details)
CABLE NUMBER | CABLE PN | FROM | TO | LABEL REQUIRED
101 | 804-1106-04 | CXEN1-PS1 | PDU A-CIRCUIT 3-POS 5 | YES
102 | 804-1106-04 | CXEN1-PS2 | PDU A-CIRCUIT 2-POS 5 | YES
103 | 804-1106-04 | CXEN1-PS3 | PDU A-CIRCUIT 1-POS 5 | YES
104 | 804-1106-03 | CXEN1-PS4 | PDU B-CIRCUIT 3-POS 5 | YES
105 | 804-1106-03 | CXEN1-PS5 | PDU B-CIRCUIT 2-POS 5 | YES
106 | 804-1106-03 | CXEN1-PS6 | PDU B-CIRCUIT 1-POS 5 | YES
107 | 804-1106-04 | CXEN2-PS1 | PDU A-CIRCUIT 3-POS 10 | YES
108 | 804-1106-04 | CXEN2-PS2 | PDU A-CIRCUIT 2-POS 10 | YES
109 | 804-1106-04 | CXEN2-PS3 | PDU A-CIRCUIT 1-POS 10 | YES
110 | 804-1106-03 | CXEN2-PS4 | PDU B-CIRCUIT 3-POS 10 | YES
111 | 804-1106-03 | CXEN2-PS5 | PDU B-CIRCUIT 2-POS 10 | YES
112 | 804-1106-03 | CXEN2-PS6 | PDU B-CIRCUIT 1-POS 10 | YES
113 | 804-0053-02 | SERVER A - A PWR | PDU A-CIRCUIT 3-POS 1 | YES
114 | 804-0053-01 | SERVER A - B PWR | PDU B-CIRCUIT 3-POS 1 | YES
115 | 804-0053-04 | SERVER B - A PWR | PDU A-CIRCUIT 2-POS 1 | YES
116 | 804-0053-03 | SERVER B - B PWR | PDU B-CIRCUIT 2-POS 1 | YES
117 | 804-0053-04 | SERVER C - A PWR | PDU A-CIRCUIT 1-POS 1 | YES
118 | 804-0053-03 | SERVER C - B PWR | PDU B-CIRCUIT 1-POS 1 | YES
119 | 804-0053-04 | SERVER D - A PWR | PDU A-CIRCUIT 3-POS 2 | YES
120 | 804-0053-03 | SERVER D - B PWR | PDU B-CIRCUIT 3-POS 2 | YES
121 | 804-0053-04 | SERVER E - A PWR | PDU A-CIRCUIT 2-POS 2 | YES
122 | 804-0053-03 | SERVER E - B PWR | PDU B-CIRCUIT 2-POS 2 | YES
123 | 804-0053-04 | SERVER F - A PWR | PDU A-CIRCUIT 1-POS 2 | YES
124 | 804-0053-03 | SERVER F - B PWR | PDU B-CIRCUIT 1-POS 2 | YES
125 | 804-0053-04 | SERVER G - A PWR | PDU A-CIRCUIT 3-POS 3 | YES
126 | 804-0053-03 | SERVER G - B PWR | PDU B-CIRCUIT 3-POS 3 | YES
127 | 804-0053-04 | SERVER H - A PWR | PDU A-CIRCUIT 2-POS 3 | YES
128 | 804-0053-03 | SERVER H - B PWR | PDU B-CIRCUIT 2-POS 3 | YES
129 | 804-0053-04 | SERVER I - A PWR | PDU A-CIRCUIT 1-POS 3 | YES
130 | 804-0053-03 | SERVER I - B PWR | PDU B-CIRCUIT 1-POS 3 | YES
131 | 804-0053-04 | SERVER J - A PWR | PDU A-CIRCUIT 3-POS 4 | YES
132 | 804-0053-03 | SERVER J - B PWR | PDU B-CIRCUIT 3-POS 4 | YES
133 | 804-0053-04 | SERVER K - A PWR | PDU A-CIRCUIT 2-POS 4 | YES
134 | 804-0053-03 | SERVER K - B PWR | PDU B-CIRCUIT 2-POS 4 | YES
135 | 804-0053-04 | SERVER L - A PWR | PDU A-CIRCUIT 1-POS 4 | YES
136 | 804-0053-03 | SERVER L - B PWR | PDU B-CIRCUIT 1-POS 4 | YES
137 | 804-0053-04 | SWITCH A - A PWR | PDU A-CIRCUIT 1-POS 8 | YES
138 | 804-0053-03 | SWITCH A - B PWR | PDU B-CIRCUIT 1-POS 8 | YES
139 | 804-0053-04 | SWITCH B - A PWR | PDU A-CIRCUIT 3-POS 8 | YES
140 | 804-0053-03 | SWITCH B - B PWR | PDU B-CIRCUIT 3-POS 8 | YES
141 | See Note 4 below | PDU A | FACILITY POWER | YES
142 | See Note 4 below | PDU B | FACILITY POWER | YES
NOTE 3: Power cables are red or blue in color. Red is A Power and Blue is B Power.
NOTE 4: Main power input cables are supplied with the PDU units. Input Power Connector on the 30 AMP PDU is a NEMA L15-30P Twist lock plug
TABLE M: POWER CABLES for use with Wright Line PDU VZIAN21650IPB 50 AMP PDU MAX Configuration is 2 enclosures and three servers or one enclosure and 12 servers. See 892-0119-01 System Interconnect NOTE: The following table will only apply if the end user has purchased the Wright Line Power Panels (See 870-3103-01 Pick List for PN and more details)
CABLE NUMBER | CABLE PN | FROM | TO | LABEL REQUIRED
101 | 804-1106-04 | CXEN1-PS1 | PDU A-CIRCUIT 1-POS 5 | YES
102 | 804-1106-04 | CXEN1-PS2 | PDU A-CIRCUIT 2-POS 3 | YES
103 | 804-1106-04 | CXEN1-PS3 | PDU A-CIRCUIT 3-POS 5 | YES
104 | 804-1106-03 | CXEN1-PS4 | PDU B-CIRCUIT 1-POS 5 | YES
105 | 804-1106-03 | CXEN1-PS5 | PDU B-CIRCUIT 2-POS 3 | YES
106 | 804-1106-03 | CXEN1-PS6 | PDU B-CIRCUIT 3-POS 5 | YES
107 | 804-1106-04 | CXEN2-PS1 | PDU A-CIRCUIT 4-POS 3 | YES
108 | 804-1106-04 | CXEN2-PS2 | PDU A-CIRCUIT 5-POS 5 | YES
109 | 804-1106-04 | CXEN2-PS3 | PDU A-CIRCUIT 6-POS 3 | YES
110 | 804-1106-03 | CXEN2-PS4 | PDU B-CIRCUIT 4-POS 3 | YES
111 | 804-1106-03 | CXEN2-PS5 | PDU B-CIRCUIT 5-POS 5 | YES
112 | 804-1106-03 | CXEN2-PS6 | PDU B-CIRCUIT 6-POS 3 | YES
113-118 | NOT USED
119 | 804-0053-02 | SERVER A - A PWR | PDU A-CIRCUIT 6-POS 4 | YES
120 | 804-0053-01 | SERVER A - B PWR | PDU B-CIRCUIT 6-POS 4 | YES
121 | 804-0053-04 | SERVER B - A PWR | PDU A-CIRCUIT 5-POS 4 | YES
122 | 804-0053-03 | SERVER B - B PWR | PDU B-CIRCUIT 5-POS 4 | YES
123 | 804-0053-04 | SERVER C - A PWR | PDU A-CIRCUIT 4-POS 4 | YES
124 | 804-0053-03 | SERVER C - B PWR | PDU B-CIRCUIT 4-POS 4 | YES
125 | 804-0053-04 | SERVER D - A PWR | PDU A-CIRCUIT 3-POS 4 | YES
126 | 804-0053-03 | SERVER D - B PWR | PDU B-CIRCUIT 3-POS 4 | YES
127 | 804-0053-04 | SERVER E - A PWR | PDU A-CIRCUIT 2-POS 4 | YES
128 | 804-0053-03 | SERVER E - B PWR | PDU B-CIRCUIT 2-POS 4 | YES
129 | 804-0053-04 | SERVER F - A PWR | PDU A-CIRCUIT 1-POS 4 | YES
130 | 804-0053-03 | SERVER F - B PWR | PDU B-CIRCUIT 1-POS 4 | YES
131 | 804-0053-04 | SERVER G - A PWR | PDU A-CIRCUIT 6-POS 1 | YES
132 | 804-0053-03 | SERVER G - B PWR | PDU B-CIRCUIT 6-POS 1 | YES
133 | 804-0053-04 | SERVER H - A PWR | PDU A-CIRCUIT 5-POS 1 | YES
134 | 804-0053-03 | SERVER H - B PWR | PDU B-CIRCUIT 5-POS 1 | YES
135 | 804-0053-04 | SERVER I - A PWR | PDU A-CIRCUIT 4-POS 1 | YES
136 | 804-0053-03 | SERVER I - B PWR | PDU B-CIRCUIT 4-POS 1 | YES
137 | 804-0053-04 | SERVER J - A PWR | PDU A-CIRCUIT 3-POS 1 | YES
138 | 804-0053-03 | SERVER J - B PWR | PDU B-CIRCUIT 3-POS 1 | YES
139 | 804-0053-04 | SERVER K - A PWR | PDU A-CIRCUIT 2-POS 1 | YES
140 | 804-0053-03 | SERVER K - B PWR | PDU B-CIRCUIT 2-POS 1 | YES
141 | 804-0053-04 | SERVER L - A PWR | PDU A-CIRCUIT 1-POS 1 | YES
142 | 804-0053-03 | SERVER L - B PWR | PDU B-CIRCUIT 1-POS 1 | YES
143 | 804-0053-04 | SWITCH A - A PWR | PDU A-CIRCUIT 6-POS 2 | YES
144 | 804-0053-03 | SWITCH A - B PWR | PDU B-CIRCUIT 6-POS 2 | YES
145 | 804-0053-04 | SWITCH B - A PWR | PDU A-CIRCUIT 5-POS 2 | YES
146 | 804-0053-03 | SWITCH B - B PWR | PDU B-CIRCUIT 5-POS 2 | YES
147 | See Note 5 below | PDU A | FACILITY POWER | YES
148 | See Note 5 below | PDU B | FACILITY POWER | YES
NOTE 5: Main power input cables are supplied with the PDU units. Power input Connector is a 7ft power cord with California Style 50 Amp, 250 Volt, 4 wire Twistlock Plug.
870-3103-01_Power Cables Tab

## DATA CABLES
DATA CABLING GENERAL NOTES:
1) USE THE APPROPRIATE TR AND SYSTEM INTERCONNECT FOR DATA CABLING AS DENOTED IN ASSEMBLY NOTE 19. THE SYSTEM INTERCONNECT DOCUMENTS SHOW A POINT TO POINT WIRING DIAGRAM FOR DATA CABLES AND CABLE ITEM NUMBERS WHERE APPLICABLE AND THE TR HAS THE CABLE TABLES WHICH WILL CONTAIN CABLE PN (IF APPLICABLE) OR SITE SPECIFIC CABLE.
2) THE SITE SPECIFIC CABLES LISTED IN THE TOPOLOGY TRs ARE CUSTOMER SPECIFIC ON HOW THE SYSTEM WILL BE INTEGRATED INTO THE CUSTOMER NETWORK. THESE CABLES ARE SITE SPECIFIC AND SHALL BE SPECIFIED BY APPLICATION ENGINEERING OR PROFESSIONAL SERVICES ENGINEERING. THE SITE SPECIFIC CABLES WILL BE TERMINATED AT SITE SO THE CABLE PN AND CABLE LABELING (TO/FROM LABEL) WILL BE SPECIFIED BY THE APPLICATION OR PROFESSIONAL SERVICES ENGINEER.
3) TOPOLOGY 1 IN REFERENCES 11 AND 12 CONTAIN AGGREGATION SWITCHES. THESE SYSTEMS WILL BE INTERNALLY WIRED AT TIME OF MANUFACTURE USING THE BASE CABLES IN THE TABLES SHOWN IN THESE REFERENCES. FOR POINT TO POINT WIRING IS SHOWN ON THE SYSTEM INTERCONNECTS TO SUPPORT TOPOLOGY 1 DEPENDING ON THE HARDWARE CONFIGURATION.
4) IN TOPOLOGY 1 THE RACKMOUNT SERVER OOBM CONNECTIONS TO SERVER A AND SERVER B WILL NOT BE TERMINATED TO THE SWITCHES. APPLICATION ENGINEERING OR PROFESSIONAL SERVICES ENGINEERING WILL BE REQUIRED TO SPECIFY THIS CONNECTION SINCE IT IS SITE SPECIFIC. IT MAY BE TERMINATED TO THE SWITCHES OR CONNECTED TO THE CUSTOMERS NETWORK. NO CABLE WILL BE ALLOCATED FOR THIS AT TIME OF MANUFACTURE.
5) TOPOLOGIES 3, 4 AND 5 ARE ALL UPLINKED TO THE CUSTOMERS NETWORK OR SWITCHES AND THIS CABLING WILL ALSO BE SPECIFIED BY THE APPLICATION OR PROFESSIONAL SERVICES ENGINEERING. IF SFP MODULES ARE REQUIRED THE SFP PART NUMBERS ARE DEFINED IN TR007055.
6) TOPOLOGY 6- THIS TOPOLOGY SUPPORTS A MANAGEMENT SERVER AND UP TO (6) SIX C7000 ENCLOSURES. ONLY THE FIRST ENCLOSURE AND SERVERS WILL BE CABLED AND CONNECTD IN THE FIRST CABINET AT TIME OF MANUFACTURE IN MORRISVILLE FACILITY. THE REMAINING ENCLOSURES WILL BE SITE SPECIFIC AND THE CABLES WILL BE SPECIFIED BY APPLICATION OR PROFESSIONAL SERVICES ENGINEERING.
7) IF REQUIRED THE ENCLOSURE SWITCHES MAY BE ONE OR ALL OF THE FOLLOWING: ◆ 3020 SWITCH (PN 804-2185-R01) USES STANDARD CAT5a (RJ-45) CABLES. ◆ 6120XG (PN 805-0189-G01) WILL REQUIRE SFP MODULES. ◆ 6125G (PN 805-0627-01) HAS 4 PORTS THAT ARE CAT5a (RJ-45) AND 4 PORTS THAT WILL REQUIRE SFP MODULES. ◆ 6125XLG (PN 7093053) HAS 8 PORTS THAT ARE SFP+ PORTS THAT WILL REQUIRE SFP MODULES. THE NUMBER OF SFP AND TYPE WILL BE DETERMINED BY THE NUMBER OF UPLINKS WHICH ARE SITE SPECIFIC ON HOW THE SYSTEM IS INTEGRATED INTO THE NETWORK. THE ADDITIONAL SFP MODULES FOR CUSTOMERS UPLINKS WILL HAVE TO BE SPECIFIED BY APPLICATION OR PROFESSIONAL SERVICES ENGINEERING. THE SPECIFICATION AND PN FOR THE SFP ARE SHOWN IN TR007055 FOR CABLE SPEED AND USAGE.
8) THE PASS THRU MODULE (PN 805-0190-G01) IS A 1G MODULE AND WILL REQUIRE CAT5A (RJ-45) CABLES. IF THE TOPOLOGIES SHOW SITE SPECIFIC CABLING THEN THE SITE SPECIFIC CABLING WILL BE SPECIFIED BY THE APPLICATION OR PROFESSIONAL SERVICES ENGINEERING.

## 870-3111-01_SINGLE PH PWR CHTS
870-3111-01_SINGLE PH PWR CHTS Tab
SYSTEM | TABLE F: SINGLE PHASE NA/JAPAN CABINET (EXGXX) POWER CONSUMPTION WITH HP RMS. MAXIMUM CONFIGURATION THREE ENCLOSURES WITH 16 BLADES EACH, TWELVE HP RMS, TWO SWITCHES (A COMBINATION OF THIS HARDWARE IS ALLOWABLE PER THE CABINET LAYOUT VIEWS - PDUS A3 AND B3 ARE DUAL PURPOSE PDUS DEPENDING ON THE CABINET CONFIGURATION). HP 642 CABINET WITH QTY 6 HP MODULAR PDUS MAX.
PDU SPECS ARE FOR THE HP PDUS | NA/JAPAN SOLUTION: PDU TEK PN 804-2062-G07 (HP PN 252663-D75) . QTY 2 PDUS PER ENCLOSURE. TOTAL WATTS PER CABINET =49,920 WATTS . EACH MODULAR PDU REQUIRES 1X50 AMP POWER FEED; TOTALING 6x50AMPS POWER FEEDS PER CABINET) . RECEPTACLE REQUIRED HUBBELL CS8269C, 50A (PDU SPECS ARE FOR THE HP PDUS) NOTE: The following table will only apply if the end user has purchased the HP Power Panels (See Pick List for PN and more details)
PDU USAGE | PDU A1 / B1 SUPPORTS ENCLOSURE 1 AND RACKMOUNT HARDWARE |  |  |  | PDU A2 / B2 SUPPORTS ENCLOSURE 2 |  |  |  | PDU A3 / B3 SUPPORTS ENCLOSURE 3 - USE THESE COLUMNS WHEN THERE IS AN ENCLOSURE 3. SEE ASSY NOTE 7. |  |  |  | PDU A3 / B3 SUPPORTS RACKMOUNT SERVERS (OPTIONAL IN PLACE OF ENCLOSURE 3) SEE ASSY NOTE 7. |  |  |  | PDU A3 / B3 SUPPORTS RACKMOUNT SERVERS (OPTIONAL IN PLACE OF ENCLOSURE 3). SEE ASSY NOTE 7.
TOTAL POWER PER PDU | PDU A1 3 X C19 OUTLETS EXTENSION BAR A1-4 MAX POWER 40 AMPS @208VAC=8,320WATTS |  | PDU B1 3 X C19 OUTLETS EXTENSION BAR B1-4 MAX POWER 40 AMPS @208VAC=8,320WATTS |  | PDU A2 4 X C19 OUTLETS NO EXTENSION BARS MAX POWER 40 AMPS @208VAC=8,320WATTS |  | PDU B2 4 X C19 OUTLETS NO EXTENSION BARS MAX POWER 40 AMPS @208VAC=8,320WATTS |  | PDU A3 4 X C19 OUTLETS EXTENSION BAR A3-4 MAX POWER 40 AMPS @208VAC=8,320WATTS |  | PDU B3 4 X C19 OUTLETS EXTENSION BAR B3-4 MAX POWER 40 AMPS @208VAC=8,320WATTS |  | PDU A3 EXTENSION BAR A3-4 PDU MAX POWER 40 AMPS @208VAC=8,320WATTS |  | PDU A3 EXTENSION BAR A3-3 PDU MAX POWER 40 AMPS @208VAC=8,320WATTS |  | PDU B3 EXTENSION BAR B3-4 PDU MAX POWER 40 AMPS @208VAC=8,320WATTS |  | PDU B3 EXTENSION BAR B3-3 PDU MAX POWER 40 AMPS @208VAC=8,320WATTS
COMPONENT | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC
CISCO 4948E-F SWITCH | 275 | 1.3221 | 275 | 1.3221
CISCO 4948E-F SWITCH | 275 | 1.3221 | 275 | 1.3221
GEN9 SERVER A | 420 | 2.0192 | 420 | 2.0192
GEN9 SERVER B | [8 empty] | 420 | 2.0192 | 420 | 2.0192 | 420 | 2.0192 |  |  | 420 | 2.0192
GEN9 SERVER C | [12 empty] | 420 | 2.0192 |  |  | 420 | 2.0192
GEN9 SERVER D | [12 empty] | 420 | 2.0192 |  |  | 420 | 2.0192
GEN9 SERVER E | [12 empty] | 420 | 2.0192 |  |  | 420 | 2.0192
GEN9 SERVER F | [12 empty] | 420 | 2.0192 |  |  | 420 | 2.0192
GEN9 SERVER G | [12 empty] | 420 | 2.0192 |  |  | 420 | 2.0192
GEN9 SERVER H | [14 empty] | 420 | 2.0192 |  |  | 420 | 2.0192
GEN9 SERVER I | [14 empty] | 420 | 2.0192 |  |  | 420 | 2.0192
GEN9 SERVER J | [14 empty] | 420 | 2.0192 |  |  | 420 | 2.0192
GEN9 SERVER K | [14 empty] | 420 | 2.0192 |  |  | 420 | 2.0192
GEN9 SERVER L | [14 empty] | 420 | 2.0192 |  |  | 420 | 2.0192
ENCL 3 PS 1 | [8 empty] | 1800 | 8.6538
ENCL 3 PS 2 | [8 empty] | 1800 | 8.6538
ENCL 3 PS 3 | [8 empty] | 1800 | 8.6538
ENCL 3 PS 4 | [10 empty] | 1800 | 8.6538
ENCL 3 PS 5 | [10 empty] | 1800 | 8.6538
ENCL 3 PS 6 | [10 empty] | 1800 | 8.6538
ENCL 2 PS 1 |  |  |  |  | 1800 | 8.6538
ENCL 2 PS 2 |  |  |  |  | 1800 | 8.6538
ENCL 2 PS 3 |  |  |  |  | 1800 | 8.6538
ENCL 2 PS 4 | [6 empty] | 1800 | 8.6538
ENCL 2 PS 5 | [6 empty] | 1800 | 8.6538
ENCL 2 PS 6 | [6 empty] | 1800 | 8.6538
ENCL 1 PS 1 | 1800 | 8.6538
ENCL 1 PS 2 | 1800 | 8.6538
ENCL 1 PS 3 | 1800 | 8.6538
ENCL 1 PS 4 |  |  | 1800 | 8.6538
ENCL 1 PS 5 |  |  | 1800 | 8.6538
ENCL 1 PS 6 |  |  | 1800 | 8.6538
TOTAL WATTS | 6370 |  | 6370 |  | 5400 |  | 5400 |  | 5820 |  | 5820 |  | 2520 |  | 2100 |  | 2520 |  | 2100
TOTAL AMPS @208VAC | 30.625 |  | 30.625 |  | 25.9615 |  | 25.9615 |  | 27.9808 |  | 27.9808 |  | 12.1154 |  | 10.0962 |  | 12.1154 |  | 10.0962
TOTAL AMPS PER PDU | 40AMPS |  | 40AMPS |  | 40AMPS |  | 40AMPS |  | 40AMPS |  | 40AMPS |  | 40AMPS |  |  |  | 40AMPS
SYSTEM | TABLE G: SINGLE PHASE INTERNATIONAL CABINET (EXGXX) POWER CONSUMPTION. MAXIMUM CONFIGURATION THREE ENCLOSURES WITH 16 BLADES EACH, TWELVE HP RMS, TWO SWITCHES (A COMBINATION OF THIS HARDWARE IS ALLOWABLE PER THE CABINET LAYOUT VIEWS - PDUS A3 AND B3 ARE DUAL PURPOSE PDUS DEPENDING ON THE CABINET CONFIGURATION). HP 642 CABINET WITH QTY 6 HP MODULAR PDUS MAX.
PDU SPECS ARE FOR THE HP PDUS | INTERNATIONAL SOLUTION: PDU TEK PN 804-2062-G04 (252663-B33) QTY 2 PDUS PER ENCLOSURE. TOTAL WATTS PER CABINET =44,160 WATTS . EACH MODULAR PDU REQUIRES 1X32 AMP POWER FEED; TOTALING 6x32AMPS POWER FEEDS PER CABINET) RECEPTACLE REQUIRED IEC60309 OR HUBBELL C332C6S (PDU SPECS ARE FOR THE HP PDUS) NOTE: The following table will only apply if the end user has purchased the HP Power Panels (See Pick List for PN and more details)
PDU USAGE | PDU A1 / B1 SUPPORTS ENCLOSURE 1 AND RACKMOUNT HARDWARE |  |  |  | PDU A2 / B2 SUPPORTS ENCLOSURE 2 |  |  |  | PDU A3 / B3 SUPPORTS ENCLOSURE 3 - USE THESE COLUMNS WHEN THERE IS AN ENCLOSURE 3. SEE ASSY NOTE 7. |  |  |  | PDU A3 / B3 SUPPORTS RACKMOUNT SERVERS (OPTIONAL IN PLACE OF ENCLOSURE 3). SEE ASSY NOTE 7. |  |  |  | PDU A3 / B3 SUPPORTS RACKMOUNT SERVERS (OPTIONAL IN PLACE OF ENCLOSURE 3). SEE ASSY NOTE 7.
TOTAL POWER PER PDU | PDU A1 3 X C19 OUTLETS EXTENSION BAR A1-4 MAX POWER 32 AMPS @230VAC=7,360WATTS |  | PDU B1 3 X C19 OUTLETS EXTENSION BAR B1-4 MAX POWER 32 AMPS @230VAC=7,360WATTS |  | PDU A2 4 X C19 OUTLETS NO EXTENSION BARS MAX POWER 32 AMPS @230VAC=7,360WATTS |  | PDU B2 4 X C19 OUTLETS NO EXTENSION BARS MAX POWER 32 AMPS @230VAC=7,360WATTS |  | PDU A3 4 X C19 OUTLETS EXTENSION BAR A3-4 MAX POWER 32 AMPS @230VAC=7,360WATTS |  | PDU B3 4 X C19 OUTLETS EXTENSION BAR B3-4 MAX POWER 32 AMPS @230VAC=7,360WATTS |  | PDU A3 EXTENSION BAR A3-4 PDU MAX POWER 32 AMPS @230VAC=7,360WATTS |  | PDU A3 EXTENSION BAR A3-3 PDU MAX POWER 32 AMPS @230VAC=7,360WATTS |  | PDU B3 EXTENSION BAR B3-4 PDU MAX POWER 32 AMPS @230VAC=7,360WATTS |  | PDU B3 EXTENSION BAR B3-3 PDU MAX POWER 32 AMPS @230VAC=7,360WATTS
COMPONENT | WATTS | AMPS @230VAC | WATTS | AMPS @230VAC | WATTS | AMPS @230VAC | WATTS | AMPS @230VAC | WATTS | AMPS @230VAC | WATTS | AMPS @230VAC | WATTS | AMPS @230VAC | WATTS | AMPS @230VAC | WATTS | AMPS @230VAC | WATTS | AMPS @230VAC
CISCO 4948E-F SWITCH | 275 | 1.1957 | 275 | 1.1957
CISCO 4948E-F SWITCH | 275 | 1.1957 | 275 | 1.1957
GEN9 SERVER A | 420 | 1.8261 | 420 | 1.8261
GEN9 SERVER B | [8 empty] | 420 | 1.8261 | 420 | 1.8261 | 420 | 1.8261 | 420 | 1.8261
GEN9 SERVER C | [12 empty] | 420 | 1.8261 |  |  | 420 | 1.8261
GEN9 SERVER D | [12 empty] | 420 | 1.8261 |  |  | 420 | 1.8261
GEN9 SERVER E | [12 empty] | 420 | 1.8261 |  |  | 420 | 1.8261
GEN9 SERVER F | [12 empty] | 420 | 1.8261 |  |  | 420 | 1.8261
GEN9 SERVER G | [12 empty] | 420 | 1.8261 |  |  | 420 | 1.8261
GEN9 SERVER H | [14 empty] | 420 | 1.8261 |  |  | 420 | 1.8261
GEN9 SERVER I | [14 empty] | 420 | 1.8261 |  |  | 420 | 1.8261
GEN9 SERVER J | [14 empty] | 420 | 1.8261 |  |  | 420 | 1.8261
GEN9 SERVER K | [14 empty] | 420 | 1.8261 |  |  | 420 | 1.8261
GEN9 SERVER L | [14 empty] | 420 | 1.8261 |  |  | 420 | 1.8261
ENCL 3 PS 1 | [8 empty] | 1800 | 7.8261
ENCL 3 PS 2 | [8 empty] | 1800 | 7.8261
ENCL 3 PS 3 | [8 empty] | 1800 | 7.8261
ENCL 3 PS 4 | [10 empty] | 1800 | 7.8261
ENCL 3 PS 5 | [10 empty] | 1800 | 7.8261
ENCL 3 PS 6 | [10 empty] | 1800 | 7.8261
ENCL 2 PS 1 |  |  |  |  | 1800 | 7.8261
ENCL 2 PS 2 |  |  |  |  | 1800 | 7.8261
ENCL 2 PS 3 |  |  |  |  | 1800 | 7.8261
ENCL 2 PS 4 | [6 empty] | 1800 | 7.8261
ENCL 2 PS 5 | [6 empty] | 1800 | 7.8261
ENCL 2 PS 6 | [6 empty] | 1800 | 7.8261
ENCL 1 PS 1 | 1800 | 7.8261
ENCL 1 PS 2 | 1800 | 7.8261
ENCL 1 PS 3 | 1800 | 7.8261
ENCL 1 PS 4 |  |  | 1800 | 7.8261
ENCL 1 PS 5 |  |  | 1800 | 7.8261
ENCL 1 PS 6 |  |  | 1800 | 7.8261
TOTAL WATTS | 6370 |  | 6370 |  | 5400 |  | 5400 |  | 5820 |  | 5820 |  | 2520 |  | 2520 |  | 2100 |  | 2100
TOTAL AMPS @230VAC | 27.6957 |  | 27.6957 |  | 23.4783 |  | 23.4783 |  | 25.3043 |  | 25.3043 |  | 10.9565 |  | 10.9565 |  | 9.1304 |  | 9.1304
TOTAL AMPS PER PDU | 32AMPS |  | 32AMPS |  | 32AMPS |  | 32AMPS |  | 32AMPS |  | 32AMPS |  | 32AMPS |  |  |  | 32AMPS

## 870-31111-01_3 PHASE PWR CHARTS
870-31111-01_3 PHASE PWR CHARTS TAB
SYSTEM | TABLE H - MAXIMUM CONFIGURATION 2 ENCLOSURES, 12 GEN9 SERVERS AND TWO 4948E-F SWITCHES USING TWO 3 -PHASE NORTH AMERICA PDU UNITS
PDU (PDU SPECS ARE FOR THE HP PDUS) | PDU UNIT PN 804-2062-G10 QUANTITY 2 PDUS PER CABINET AND TOTAL WATTS =28,786W AT 208V, (69A, 23A PER PHASE) RECEPTABLE REQUIRED- 208V 3 PHASE 3 POLE 4 WIRE (DELTA) CS8364C, CS8369 OR EQUIVALENT (QTY 2) (PDU SPECS ARE FOR THE HP PDUS) NOTE: The following table will only apply if the end user has purchased the HP Power Panels (See Pick List for PN and more details)
PDU 7X C-13 OUTLETS MAX POWER 12AMPS @ 208VAC=2,496WATTS | PDU A1 | [7 empty] | PDU B1 | [7 empty] | PDU A2 | [7 empty] | PDU B2
| PDU BREAKERS A1-1 THRU A1-3 |  | PDU EXT BAR A1-4 |  | PDU EXT BAR A1-5 |  | PDU EXT BAR A1-6 |  | PDU BREAKERS B1-1 THRU B1-3 |  | PDU EXT BAR B1-4 |  | PDU EXT BAR B1-5 |  | PDU EXT BAR B1-6 |  | PDU BREAKERS A2-1 THRU A2-3 |  | PDU EXT BAR A2-4 |  | PDU EXT BAR A2-5 |  | PDU EXT BAR A2-6 |  | PDU BREAKERS B2-1 THRU B2-3 |  | PDU EXT BAR B2-4 |  | PDU EXT BAR B2-5 |  | PDU EXT BAR B2-6
COMPONENT | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC
SWITCH B CISCO 4948E-F | [6 empty] | 275 | 1.3221 | [6 empty] | 275 | 1.3221
SWITCH A CISCO 4948E-F |  |  |  |  | 275 | 1.3221 | [6 empty] | 275 | 1.3221
GEN9 SERVER A |  |  |  |  | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER B | [6 empty] | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER C |  |  | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER D |  |  | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER E | [6 empty] | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER F |  |  |  |  | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER G |  |  | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER H | [6 empty] | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER I |  |  |  |  | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER J |  |  | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER K |  |  | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER L |  |  | 420 | 2.0192 | [6 empty] | 420 | 2.0192
ENCL 3 PS 1
ENCL 3 PS 2
ENCL 3 PS 3
ENCL 3 PS 4
ENCL 3 PS 5
ENCL 3 PS 6
ENCL 2 PS 1 | [16 empty] | 1800 | 8.6538
ENCL 2 PS 2 | [16 empty] | 1800 | 8.6538
ENCL 2 PS 3 | [16 empty] | 1800 | 8.6538
ENCL 2 PS 4 | [24 empty] | 1800 | 8.6538
ENCL 2 PS 5 | [24 empty] | 1800 | 8.6538
ENCL 2 PS 6 | [24 empty] | 1800 | 8.6538
ENCL 1 PS 1 | 1800 | 8.6538
ENCL 1 PS 2 | 1800 | 8.6538
ENCL 1 PS 3 | 1800 | 8.6538
ENCL 1 PS 4 | [8 empty] | 1800 | 8.6538
ENCL 1 PS 5 | [8 empty] | 1800 | 8.6538
ENCL 1 PS 6 | [8 empty] | 1800 | 8.6538
TOTAL WATTS | 5400 |  | 2520 |  | 1535 |  | 1535 |  | 5400 |  | 2520 |  | 1535 |  | 1535 |  | 5400 |  | 0 |  | 0 |  | 0 |  | 5400 |  | 0 |  | 0 |  | 0
TOTAL AMPS @208VAC | 25.9615 |  | 12.1154 |  | 7.3798 |  | 7.3798 |  | 25.9615 |  | 12.1154 |  | 7.3798 |  | 7.3798 |  | 25.9615 |  | 0 |  | 0 |  | 0 |  | 25.9615 |  | 0 |  | 0 |  | 0
TOTAL AMPS PER PDU EXTENSION BAR | 60 AMPS |  | 20 AMPS |  | 20 AMPS |  | 20 AMPS |  | 60 AMPS |  | 20 AMPS |  | 20 AMPS |  | 20 AMPS |  | 60 AMPS |  | 20 AMPS |  | 20 AMPS |  | 20 AMPS |  | 60 AMPS |  | 20 AMPS |  | 20 AMPS |  | 20 AMPS
SYSTEM | TABLE J - MAXIMUM CONFIGURATION 3 ENCLOSURES, 2 GEN9 SERVERS AND TWO 4948E-F SWITCHES USING TWO 3 -PHASE NORTH AMERICA PDU UNITS
PDU (PDU SPECS ARE FOR THE HP PDUS) | PDU UNIT PN 804-2062-G11 QUANTITY 2 PDUS PER CABINET AND TOTAL WATTS =28,786W AT 208V, (69A, 23A PER PHASE) RECEPTABLE REQUIRED- 208V 3 PHASE 3 POLE 4 WIRE (DELTA) CS8364C, CS8369 OR EQUIVALENT (QTY 2) (PDU SPECS ARE FOR THE HP PDUS) NOTE: The following table will only apply if the end user has purchased the HP Power Panels (See Pick List for PN and more details)
PDU 7X C-13 OUTLETS MAX POWER 12AMPS @ 208VAC=2,496WATTS | PDU A1 | [7 empty] | PDU B1 | [7 empty] | PDU A2 | [7 empty] | PDU B2
| PDU BREAKERS A1-1 THRU A1-3 |  | PDU EXT BAR A1-4 |  | PDU EXT BAR A1-5 |  | PDU EXT BAR A1-6 |  | PDU BREAKERS B1-1 THRU B1-3 |  | PDU EXT BAR B1-4 |  | PDU EXT BAR B1-5 |  | PDU EXT BAR B1-6 |  | PDU BREAKERS A2-1 THRU A2-3 |  | PDU EXT BAR A2-4 |  | PDU EXT BAR A2-5 |  | PDU EXT BAR A2-6 |  | PDU BREAKERS B2-1 THRU B2-3 |  | PDU EXT BAR B2-4 |  | PDU EXT BAR B2-5 |  | PDU EXT BAR B2-6
COMPONENT | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC
SWITCH B CISCO 4948E-F | [6 empty] | 275 | 1.3221 | [6 empty] | 275 | 1.3221
SWITCH A CISCO 4948E-F |  |  |  |  | 275 | 1.3221 | [6 empty] | 275 | 1.3221
GEN9 SERVER A |  |  |  |  | 420 | 2.0192 | [6 empty] | 420 | 2.0192
GEN9 SERVER B | [6 empty] | 420 | 2.0192 | [6 empty] | 420 | 2.0192
ENCL 3 PS 1 |  |  | 1800 | 8.6538
ENCL 3 PS 2 | [18 empty] | 1800 | 8.6538
ENCL 3 PS 3 | [20 empty] | 1800 | 8.6538
ENCL 3 PS 4 | [10 empty] | 1800 | 8.6538
ENCL 3 PS 5 | [28 empty] | 1800 | 8.6538
ENCL 3 PS 6 | [30 empty] | 1800 | 8.6538
ENCL 2 PS 1 | [16 empty] | 1800 | 8.6538
ENCL 2 PS 2 | [16 empty] | 1800 | 8.6538
ENCL 2 PS 3 | [16 empty] | 1800 | 8.6538
ENCL 2 PS 4 | [24 empty] | 1800 | 8.6538
ENCL 2 PS 5 | [24 empty] | 1800 | 8.6538
ENCL 2 PS 6 | [24 empty] | 1800 | 8.6538
ENCL 1 PS 1 | 1800 | 8.6538
ENCL 1 PS 2 | 1800 | 8.6538
ENCL 1 PS 3 | 1800 | 8.6538
ENCL 1 PS 4 | [8 empty] | 1800 | 8.6538
ENCL 1 PS 5 | [8 empty] | 1800 | 8.6538
ENCL 1 PS 6 | [8 empty] | 1800 | 8.6538
TOTAL WATTS | 5400 |  | 1800 |  | 695 |  | 695 |  | 5400 |  | 1800 |  | 695 |  | 695 |  | 5400 |  | 1800 |  | 1800 |  | 0 |  | 5400 |  | 0 |  | 1800 |  | 1800
TOTAL AMPS @208VAC | 25.9615 |  | 8.6538 |  | 3.3413 |  | 3.3413 |  | 25.9615 |  | 8.6538 |  | 3.3413 |  | 3.3413 |  | 25.9615 |  | 8.6538 |  | 8.6538 |  | 0 |  | 25.9615 |  | 0 |  | 8.6538 |  | 8.6538
TOTAL AMPS PER PDU EXTENSION BAR | 60 AMPS |  | 20 AMPS |  | 20 AMPS |  | 20 AMPS |  | 60 AMPS |  | 20 AMPS |  | 20 AMPS |  | 20 AMPS |  | 60 AMPS |  | 20 AMPS |  | 20 AMPS |  | 20 AMPS |  | 60 AMPS |  | 20 AMPS |  | 20 AMPS |  | 20 AMPS

## 870-3103-01_Power Charts
SYSTEM | TABLE N: 50 amp -3 Phase Delta Monitored PDU (17110314) WITH HP SERVERS MAXIMUM CONFIGURATION THREE ENCLOSURES WITH 12 DL380 GEN9 Servers
PDU PART NUMBER AND SPECIFICATION | Wright Line PN Product: 17110314 part of 50 AMP PDU Kit ORACLE PN 805-0584-01 Description: 62” Vertical, 50Amps @ 250V 3~ Delta, 12 IEC type C-13 receptacles, 12 IEC type C-19 receptacles, 10ft power cord with California Style 50 Amp, 250 Volt, 4 wire Twistlock Plug, 3 20Amp 20 AMP Triple Pole Magnetic Breakers, 1 Input, Voltage 250 Delta, Amperage 50 x 3 Phase DELTA, VA per Input 21,625 (50 x 250 x SQRT(3)), Frequency 50/60 Hz, Over Current Protection (3) 20 AMP Triple Pole Magnetic Breakers
PDU Designation | PDU A | [5 empty] | PDU B
PDU CIRCUIT | Circuit 1 3 X C19 OUTLETS 6 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS |  | Circuit 2 3 X C19 OUTLETS 6 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS |  | Circuit 3 6 X C19 OUTLETS 3 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS |  | Circuit 1 3 X C19 OUTLETS 6 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS |  | Circuit 2 3 X C19 OUTLETS 6 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS |  | Circuit 3 6 X C19 OUTLETS 3 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS
COMPONENT | WATTS | AMPS @250VAC | WATTS | AMPS @250VAC | WATTS | AMPS @250VAC | WATTS | AMPS @250VAC | WATTS | AMPS @250VAC | WATTS | AMPS @250VAC
CISCO 4948E-F SWITCH B |  |  |  |  | 275 | 1.1 |  |  |  |  | 275 | 1.1
CISCO 4948E-F SWITCH A | 275 | 1.1 |  |  |  |  | 275 | 1.1
DL380 GEN9 SERVER L |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER K |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER J |  |  |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER I | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER H |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER G |  |  |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER F | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER E |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER D |  |  |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER C | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER B |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER A |  |  |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
EN1 C7000 PS1 | 1800 | 7.2
EN1 C7000 PS2 |  |  | 1800 | 7.2
EN1 C7000 PS3 |  |  |  |  | 1800 | 7.2
EN1 C7000 PS4 | [6 empty] | 1800 | 7.2
EN1 C7000 PS5 | [8 empty] | 1800 | 7.2
EN1 C7000 PS6 | [10 empty] | 1800 | 7.2
TOTAL WATTS | 3335 |  | 3900 |  | 3755 |  | 3335 |  | 3900 |  | 3755
TOTAL AMPS @250VAC WITH ONE C7000 ENCLOSURE AND 12 SERVERS | 13.34 |  | 15.6 |  | 15.02 |  | 13.34 |  | 15.6 |  | 15.02
TOTAL AMPS @250VAC WITH TWO C7000 ENCLOSURE AND 3 SERVERS | 17.18 |  | 16.08 |  | 17.18 |  | 17.18 |  | 16.08 |  | 17.18
TOTAL AMPS ALLOWED PER PDU | 20AMPS |  | 20AMPS |  | 20AMPS |  | 20AMPS |  | 20AMPS |  | 20AMPS
SYSTEM | TABLE P: 30 amp -3 Phase Delta Monitored PDU (17110217) WITH HP SERVERS MAXIMUM CONFIGURATION THREE ENCLOSURES WITH 12 DL380 GEN9 Servers
PDU PART NUMBER AND SPECIFICATION | Wright Line PN Product: 17110217 part of 805-0582-01 and 805-0562-01 Wright Line Cabinet Assy Description: 62” Vertical, 30Amps @ 250V 3~ Delta, 24 IEC type C-13 receptacles, 6 IEC type C-19 receptacles, 10ft power cord with NEMA L15-30P Twist lock plug, 3 20Amp double pole magnetic breakers/switches
PDU Designation | PDU A | [5 empty] | PDU B
PDU CIRCUIT | Circuit 1 2 X C19 OUTLETS 8 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS |  | Circuit 2 2 X C19 OUTLETS 8 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS |  | Circuit 3 2 X C19 OUTLETS 8 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS |  | Circuit 1 2 X C19 OUTLETS 8 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS |  | Circuit 2 2 X C19 OUTLETS 8 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS |  | Circuit 3 2 X C19 OUTLETS 8 X C13 OUTLETS MAX POWER 20 AMPS @250VAC=5,000WATTS
COMPONENT | WATTS | AMPS @250VAC | WATTS | AMPS @250VAC | WATTS | AMPS @250VAC | WATTS | AMPS @250VAC | WATTS | AMPS @250VAC | WATTS | AMPS @250VAC
CISCO 4948E-F SWITCH B |  |  |  |  | 275 | 1.1 |  |  |  |  | 275 | 1.1
CISCO 4948E-F SWITCH A | 275 | 1.1 |  |  |  |  | 275 | 1.1
DL380 GEN9 SERVER L | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER K |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER J |  |  |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER I | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER H |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER G |  |  |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER F | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER E |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER D |  |  |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER C | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER B |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
DL380 GEN9 SERVER A |  |  |  |  | 420 | 1.68 |  |  |  |  | 420 | 1.68
EN1 C7000 PS1 | 1800 | 7.2
EN1 C7000 PS2 |  |  | 1800 | 7.2
EN1 C7000 PS3 |  |  |  |  | 1800 | 7.2
EN1 C7000 PS4 | [6 empty] | 1800 | 7.2
EN1 C7000 PS5 | [8 empty] | 1800 | 7.2
EN1 C7000 PS6 | [10 empty] | 1800 | 7.2
TOTAL WATTS | 3755 |  | 3480 |  | 3755 |  | 3755 |  | 3480 |  | 3755
TOTAL AMPS @250VAC -PER CIRCUIT WITH ONE C7000 ENCLOSURE AND 12 SERVERS | 15.02 |  | 13.92 |  | 15.02 |  | 15.02 |  | 13.92 |  | 15.02
TOTAL AMPS @250VAC -PER CIRCUIT WITH TWO C7000 ENCLOSURE AND 3 SERVERS | 17.18 |  | 16.08 |  | 17.18 |  | 17.18 |  | 16.08 |  | 17.18
MAX AMPS ALLOWED PER CIRCUIT | 20AMPS |  | 20AMPS |  | 20AMPS |  | 20AMPS |  | 20AMPS |  | 20AMPS
SYSTEM | TABLE R: 50 amp -3 Phase Delta Monitored Wright Line PDU VZIAN21650IPB WITH HP SERVERS MAXIMUM CONFIGURATION TWO ENCLOSURES, THREE DL380 SERVERS AND TWO SWITCHES; OR, ONE ENCLOSURE, TWELVE DL380 SERVERS AND TWO SWITCHES
PDU PART NUMBER AND SPECIFICATION | Wright Line PN Product: VZIAN21650IPB part of 50 AMP PDU Kit ORACLE PN 7095212 Description: 67” Vertical, 50Amps @ 208V 3~ Delta, 21 IEC type C-13 receptacles, 6 IEC type C-19 receptacles, 7ft power cord with CS8365CP California Style 50 Amp, 208 Volt, 4 wire Twistlock Plug, 6 20Amp Breakers, 1 Input, Voltage 208 Delta, Amperage 50 x 3 Phase DELTA, VA per Input 18,013 (50 x 208 x SQRT(3)), Frequency 50/60 Hz, Over Current Protection (6) 20 AMP Triple Pole Magnetic Breakers
PDU Designation | PDU A | [11 empty] | PDU B
PDU CIRCUIT | Circuit 1 1 X C19 OUTLETS 4 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 2 1 X C19 OUTLETS 3 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 3 1 X C19 OUTLETS 4 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 4 1 X C19 OUTLETS 3 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 5 1 X C19 OUTLETS 4 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 6 1 X C19 OUTLETS 3 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 1 1 X C19 OUTLETS 4 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 2 1 X C19 OUTLETS 3 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 3 1 X C19 OUTLETS 4 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 4 1 X C19 OUTLETS 3 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 5 1 X C19 OUTLETS 4 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS |  | Circuit 6 1 X C19 OUTLETS 3 X C13 OUTLETS MAX LOAD 16 AMPS @208VAC=3,328WATTS
COMPONENT | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC | WATTS | AMPS @208VAC
CISCO 4948E-F SWITCH B | [8 empty] | 275 | 1.3221 | [10 empty] | 275 | 1.3221
CISCO 4948E-F SWITCH A | [10 empty] | 275 | 1.3221 | [10 empty] | 275 | 1.3221
DL380 GEN9 SERVER L | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER K |  |  | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER J |  |  |  |  | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER I | [6 empty] | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER H | [8 empty] | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER G | [10 empty] | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER F | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER E |  |  | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER D |  |  |  |  | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER C | [6 empty] | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER B | [8 empty] | 420 | 2.0192 | [10 empty] | 420 | 2.0192
DL380 GEN9 SERVER A | [10 empty] | 420 | 2.0192 | [10 empty] | 420 | 2.0192
EN2 C7000 PS1 | [6 empty] | 1800 | 8.6538
EN2 C7000 PS2 | [8 empty] | 1800 | 8.6538
EN2 C7000 PS3 | [10 empty] | 1800 | 8.6538
EN2 C7000 PS4 | [18 empty] | 1800 | 8.6538
EN2 C7000 PS5 | [20 empty] | 1800 | 8.6538
EN2 C7000 PS6 | [22 empty] | 1800 | 8.6538
EN1 C7000 PS1 | 1800 | 8.6538
EN1 C7000 PS2 |  |  | 1800 | 8.6538
EN1 C7000 PS3 |  |  |  |  | 1800 | 8.6538
EN1 C7000 PS4 | [12 empty] | 1800 | 8.6538
EN1 C7000 PS5 | [14 empty] | 1800 | 8.6538
EN1 C7000 PS6 | [16 empty] | 1800 | 8.6538
TOTAL WATTS | 2640 |  | 2640 |  | 2640 | [7 empty] | 2640 |  | 2640 |  | 2640 |  | 2640 |  | 2915 |  | 2915
TOTAL AMPS @208VAC WITH ONE C7000 ENCLOSURE AND 12 SERVERS | 12.6923 |  | 12.6923 |  | 12.6923 |  | 12.6923 |  | 14.0144 |  | 14.0144 |  | 12.6923 |  | 12.6923 |  | 12.6923 |  | 12.6923 |  | 14.0144 |  | 14.0144
TOTAL AMPS ALLOWED PER PDU | 16AMPS |  | 16AMPS |  | 16AMPS |  | 16AMPS |  | 16AMPS |  | 16AMPS |  | 16AMPS |  | 16AMPS |  | 16AMPS |  | 16AMPS |  | 16AMPS |  | 16AMPS
870-3103-01 Power Charts Tab

## 870-3111-01_Cabinet Footprint
870-3111-01_CABINET FOOTPRINT TAB
FIGURE 40: CABINET FOOTPRINT 870-3111-01
HP 642 1075mm Shock Intelligent Series Rack
| Dimensions (HxDxW) Total Cabinet Area | 78.816 x 42.741 x 23.535 in (200.19 x 108.56 x 59.78 cm)
| Shipping (with packaging materials) | 85.35 x 50.87 x 35.43 in (216.80 x 129.20 x 90 cm)
| Weight Operating | 378 lb (170.50 kg) (empty cabinet)
| Shipping Weight | 587 lb (265 kg)
| Shipping - Max | 2500 lb (1134 kg)
| Load Static | 3000 lb (1361 kg)
| Dynamic | 2500 lb
Color Doors Black
78.741
42.741
Tekelec Part Number
805-0614-01 HP BW904A_642 1075MM_SHOCK INTELLIGENT SERIES RACK

## 870-3103-01_Cabinet Footprint
FIGURE 52: Cabinet Footprint for Wright Line cabinets with TOC 870-3103-01
FIGURE 53: Cabinet Footprint for Wright Line cabinets without TOC 870-3103-01
870-3103-01_Cabinet Footprint Tab

## 870-3111-01_Transit_Ship Info
870-3111-01_Transit_Ship Info TAB
FIGURE 55: INSTALLATION OF THE TRANSIT BRACKETS FOR 870-3111-01
Note: The transit brackets are supplied with the cabinet and should be installed as shown.